## Notes
Monitoring was installed on 4 home supply points. All monitors were calibrated for voltage within ±0.2% and current within ±1%.
The historical readings are a worst case reading within each hour block of time. I.E. if at anytime the voltage dropped to 200.3v at any time during the hour, this is the min value that would be recorded for that time slot. The same for maximum values.
Current readings are indicative of the overall load on the system in general, but are not the total on the complete supply cable. This was not available due to dangers of accessing the transformer end supply.
On the morning of 24th Aug it is believed that monitoring was installed by the supply authority.
Two of the monitors stopped recording on 4th September for unknown reasons.
Regular dips in voltage are evident during evening periods of heavy load. These dips are beyond the normal supply voltage range of 230 +10% and -6%.

## Data
Date | Time | Home No.52 Current Min (A) | Home No.52 Current Max (A) | Home No.52 Voltage Min (V) | Home No.52 Voltage Max (V) | Home No.6 Current Min (A) | Home No.6 Current Max (A) | Home No.6 Voltage Min (V) | Home No.6 Voltage Max (V) | Home No.11 Current Min (A) | Home No.11 Current Max (A) | Home No.11 Voltage Min (V) | Home No.11 Voltage Max (V) | Home No.4 Current Min (A) | Home No.4 Current Max (A) | Home No.4 Voltage Min (V) | Home No.4 Voltage Max (V)
Styles
[5 empty] | 189 | less than 190v
[5 empty] | 200 | less than 216.2v
[5 empty] | 230 | normal
[5 empty] | 260 | greater than 253v
2026-08-07 | 14:00:00 | 0 | 3.4 | 0 | 244.28 | 1.68 | 13.19 | 228.4 | 241.7 |  |  |  |  | 0 | 0 | 227.4 | 238.7
2026-08-07 | 15:00:00 | 1.4 | 12.9 | 214.79 | 241.1 | 1.12 | 5.19 | 214.4 | 239.7 | 0 | 4.5 | 214.9 | 244.1 | 0 | 0 | 216.7 | 240.5
2026-08-07 | 16:00:00 | 1.4 | 23.2 | 210 | 235.44 | 2.3 | 16.58 | 211.7 | 233.1 | 1.09 | 1.19 | 211.9 | 231.9 | 0 | 0 | 209.8 | 233.6
2026-08-07 | 17:00:00 | 3 | 14.5 | 206.64 | 237.33 | 2.69 | 14.94 | 204.6 | 236 | 0.78 | 1.23 | 205.1 | 236.3 | 0 | 0 | 204.2 | 233
2026-08-07 | 18:00:00 | 2.7 | 19.3 | 218.06 | 241.99 | 2.52 | 10.92 | 221.3 | 241.7 | 0.59 | 0.91 | 221.6 | 242.6 | 0 | 0 | 223 | 238.7
2026-08-07 | 19:00:00 | 1.6 | 18.2 | 217.37 | 243.19 | 2.16 | 13.45 | 220.7 | 242.6 | 0.59 | 1.04 | 220.9 | 242.7 | 0 | 0 | 220.4 | 240.5
2026-08-07 | 20:00:00 | 1.6 | 3 | 229.88 | 238.62 | 2.08 | 4.14 | 230 | 238.2 | 0.69 | 1.92 | 230.6 | 237.5 | 0 | 0 | 226.8 | 238.4
2026-08-07 | 21:00:00 | 1.6 | 2.8 | 227.89 | 240.21 | 1.83 | 2.88 | 228.8 | 240.2 | 0.54 | 0.93 | 228.8 | 240 | 0 | 0 | 228.4 | 239.3
2026-08-07 | 22:00:00 | 1.1 | 3.5 | 230.77 | 242.79 | 1.72 | 2.45 | 232.6 | 242.4 | 0.53 | 0.55 | 232.4 | 242.7 | 0 | 0 | 230.5 | 243.2
2026-08-07 | 23:00:00 | 1 | 3.4 | 230.67 | 242.89 | 1.41 | 1.96 | 234.3 | 241.7 | 0.29 | 0.55 | 234.5 | 242.1 | 0 | 0 | 236.1 | 242.9
2026-08-08 | 00:00:00 | 1.1 | 3.8 | 235.04 | 242.89 | 1.36 | 5.93 | 236.6 | 242.2 | 0.29 | 0.31 | 236.8 | 242.4 | 0 | 0 | 237.6 | 242.9
2026-08-08 | 01:00:00 | 0.8 | 2.4 | 238.32 | 243.88 | 1.36 | 1.7 | 238.5 | 243.7 | 0.28 | 0.33 | 238.9 | 243.8 | 0 | 0 | 238 | 239.6
2026-08-08 | 02:00:00 | 0.8 | 3.7 | 237.53 | 245.37 | 1.35 | 2.22 | 238.2 | 244 | 0.31 | 0.7 | 238.2 | 244.3 | 0 | 0 | 234.4 | 244.9
2026-08-08 | 03:00:00 | 1 | 3.7 | 237.03 | 242.99 | 1.36 | 1.77 | 237.2 | 242.9 | 0.28 | 0.57 | 237 | 243 | 0 | 0 | 239 | 241.4
2026-08-08 | 04:00:00 | 0.9 | 3.8 | 230.08 | 243.29 | 1.35 | 2.48 | 227.5 | 242.8 | 0.29 | 0.3 | 228.6 | 242.8 | 0 | 0 | 225.8 | 241.4
2026-08-08 | 05:00:00 | 0.9 | 13.3 | 226.11 | 243.88 | 1.34 | 12.34 | 226.4 | 243.7 | 0.29 | 11.63 | 225.8 | 244.1 | 0 | 0 | 226.8 | 244.1
2026-08-08 | 06:00:00 | 0.8 | 12.7 | 226.5 | 242.79 | 1.54 | 13.95 | 223.8 | 241.7 | 0.56 | 5.39 | 224.2 | 242.2 | 0 | 0 | 223.7 | 243.2
2026-08-08 | 07:00:00 | 1 | 12.7 | 222.93 | 245.97 | 1.31 | 14.31 | 218.6 | 245.5 | 0.31 | 9.6 | 218.4 | 244.9 | 0 | 0 | 217.7 | 244.4
2026-08-08 | 08:00:00 | 1 | 12 | 213.79 | 253.02 | 1.77 | 11.45 | 219.6 | 252.3 | 0.3 | 0.33 | 219.5 | 253.1 | 0 | 0 | 220.4 | 252.3
2026-08-08 | 09:00:00 | 0.9 | 12.8 | 215.28 | 243.29 | 1.8 | 13.74 | 215 | 242.4 | 0.31 | 0.71 | 214.9 | 241.7 | 0 | 0 | 214.6 | 240.5
2026-08-08 | 10:00:00 | 1 | 13.2 | 220.94 | 241.7 | 1.8 | 13.57 | 218.7 | 240.8 | 0.56 | 6.96 | 218.6 | 241.2 | 0 | 0 | 219.7 | 239.1
2026-08-08 | 11:00:00 | 1 | 13 | 216.47 | 240.8 | 2.04 | 22.81 | 218.1 | 240.1 | 0.54 | 0.58 | 218 | 240.3 | 0 | 0 | 217.5 | 240.2
2026-08-08 | 12:00:00 | 1.3 | 12.3 | 213.5 | 237.92 | 2.16 | 21.53 | 215 | 237.3 | 0.53 | 0.57 | 214.7 | 237.5 | 0 | 0 | 215.3 | 238.2
2026-08-08 | 13:00:00 | 1.6 | 23.8 | 215.18 | 237.33 | 2.01 | 10.44 | 218.9 | 236.2 | 0.53 | 0.56 | 219.7 | 236.9 | 0 | 0 | 220.1 | 235.6
2026-08-08 | 14:00:00 | 1.5 | 9.1 | 211.01 | 236.63 | 1.95 | 10.91 | 210.1 | 235.8 | 0.3 | 9.42 | 209.8 | 235.9 | 0 | 0 | 211.6 | 235.9
2026-08-08 | 15:00:00 | 1.5 | 19.5 | 211.81 | 234.25 | 1.71 | 24.51 | 209.5 | 234.1 | 0.82 | 9.56 | 209 | 233.8 | 0 | 0 | 210.5 | 231.7
2026-08-08 | 16:00:00 | 8 | 23.3 | 197.11 | 229.58 | 1.71 | 5.67 | 197.1 | 228.9 | 0.81 | 1.39 | 197.1 | 229.1 | 0 | 0 | 198.4 | 229.8
2026-08-08 | 17:00:00 | 2.2 | 18.2 | 200.69 | 223.62 | 3.72 | 8.52 | 202.2 | 224.1 | 1.08 | 1.23 | 203.7 | 224.1 | 0 | 0 | 203.5 | 221.7
2026-08-08 | 18:00:00 | 1.8 | 17.9 | 199.39 | 231.77 | 2.71 | 4.48 | 201.1 | 231.4 | 0.85 | 1.21 | 201 | 232.6 | 0 | 0 | 201 | 233.6
2026-08-08 | 19:00:00 | 1.6 | 14.1 | 214.69 | 235.14 | 1.96 | 7.51 | 216.4 | 236.5 | 0.56 | 0.92 | 216.3 | 237 | 0 | 0 | 219.7 | 234.2
2026-08-08 | 20:00:00 | 1.6 | 4.9 | 221.94 | 236.33 | 1.76 | 13.95 | 221.7 | 238.6 | 0.5 | 1.12 | 221.9 | 237.6 | 0 | 0 | 221.4 | 238.3
2026-08-08 | 21:00:00 | 2.5 | 3.2 | 226.8 | 235.84 | 2.25 | 3.25 | 228.7 | 237.3 | 0.39 | 0.84 | 228.8 | 237 | 0 | 0 | 227.1 | 236.7
2026-08-08 | 22:00:00 | 1.4 | 4.6 | 222.83 | 235.54 | 1.49 | 6.17 | 223 | 236.5 | 0.55 | 0.6 | 222.9 | 236.7 | 0 | 0 | 224.5 | 236.7
2026-08-08 | 23:00:00 | 0.9 | 3.2 | 227.89 | 238.42 | 1.36 | 5.49 | 229.3 | 239.4 | 0.28 | 0.56 | 228.8 | 239.6 | 0 | 0 | 225.5 | 238.7
2026-08-09 | 00:00:00 | 0.9 | 4.1 | 232.86 | 241.8 | 1.36 | 2.48 | 235.4 | 241.9 | 0.28 | 0.3 | 235.1 | 242 | 0 | 0 | 236.4 | 242.6
2026-08-09 | 01:00:00 | 1 | 3.5 | 239.02 | 243.48 | 1.5 | 2.03 | 237.5 | 243.4 | 0.28 | 0.68 | 238.8 | 243.5 | 0 | 0 | 235.6 | 242.6
2026-08-09 | 02:00:00 | 0.8 | 1.3 | 239.11 | 243.38 | 1.45 | 1.78 | 239.6 | 243.1 | 0.53 | 0.59 | 239.1 | 243.3 | 0 | 0 | 239.6 | 240.8
2026-08-09 | 03:00:00 | 1.1 | 3.8 | 238.22 | 243.38 | 1.36 | 3.53 | 238.5 | 243 | 0.28 | 0.55 | 238.8 | 243 | 0 | 0 | 235.9 | 241.4
2026-08-09 | 04:00:00 | 0.8 | 12.1 | 227.69 | 245.37 | 1.33 | 12.71 | 226.7 | 245.2 | 0.28 | 11.67 | 226.2 | 245.8 | 0 | 0 | 230 | 243.9
2026-08-09 | 05:00:00 | 1 | 12.2 | 226.3 | 243.19 | 1.36 | 5.63 | 226.2 | 242.8 | 0.29 | 1.15 | 226.4 | 243.1 | 0 | 0 | 225.5 | 242.6
2026-08-09 | 06:00:00 | 1.2 | 12.6 | 222.43 | 243.09 | 1.48 | 10.18 | 222.1 | 242.1 | 0.56 | 4.6 | 221.4 | 242.5 | 0 | 0 | 224 | 239.9
2026-08-09 | 07:00:00 | 0.9 | 11.7 | 218.76 | 240.8 | 1.67 | 13.85 | 221.6 | 240.1 | 0.56 | 1.15 | 220.8 | 239.9 | 0 | 0 | 219.4 | 239
2026-08-09 | 08:00:00 | 1.1 | 22.4 | 210.02 | 240.6 | 2.39 | 11.73 | 211.3 | 239.2 | 0.54 | 9.46 | 210.2 | 239.4 | 0 | 0 | 209.2 | 239.6
2026-08-09 | 09:00:00 | 1.6 | 22.8 | 208.23 | 244.28 | 2.44 | 13.77 | 211.3 | 243 | 0.31 | 0.61 | 211.7 | 243.5 | 0 | 0 | 212.8 | 243.5
2026-08-09 | 10:00:00 | 1.4 | 22.2 | 213.2 | 245.67 | 2.69 | 20.95 | 215.1 | 244.7 | 0.3 | 0.33 | 215 | 244.7 | 0 | 0 | 217.6 | 244.6
2026-08-09 | 11:00:00 | 1.6 | 20.9 | 206.44 | 238.32 | 2.8 | 15.57 | 210 | 238.1 | 0.31 | 8.38 | 210.5 | 237.6 | 0 | 0 | 211.6 | 238.2
2026-08-09 | 12:00:00 | 1.8 | 20.1 | 214.19 | 238.32 | 2.98 | 14.84 | 212.3 | 237.4 | 0.55 | 0.64 | 212.5 | 237.5 | 0 | 0 | 212.5 | 238.2
2026-08-09 | 13:00:00 | 1.5 | 13.7 | 214.69 | 238.12 | 3.48 | 12.46 | 213.9 | 237 | 0.55 | 1.14 | 213.8 | 237.1 | 0 | 0 | 214.4 | 238.2
2026-08-09 | 14:00:00 | 1.6 | 13.1 | 220.05 | 235.94 | 3.48 | 15.82 | 219 | 234 | 0.86 | 12.67 | 219.3 | 233.6 | 0 | 0 | 219.4 | 233.9
2026-08-09 | 15:00:00 | 1.6 | 3.7 | 213.1 | 238.82 | 2.34 | 9.39 | 207.4 | 237.5 | 1.01 | 6.81 | 207.4 | 238.2 | 0 | 0 | 204.5 | 238.9
2026-08-09 | 16:00:00 | 1.7 | 13.2 | 211.91 | 233.45 | 3.16 | 8.21 | 205.2 | 231.3 | 1.08 | 1.56 | 208.3 | 231.2 | 0 | 0 | 208.5 | 230.6
2026-08-09 | 17:00:00 | 7.8 | 15.7 | 211.61 | 230.18 | 2.63 | 3.98 | 214.6 | 229.1 | 1.27 | 1.5 | 214.2 | 230 | 0 | 0 | 217.3 | 230
2026-08-09 | 18:00:00 | 3.1 | 18.9 | 204.86 | 231.96 | 2.22 | 14.58 | 204.4 | 229.9 | 0.84 | 1.5 | 204.4 | 230.5 | 0 | 0 | 202.8 | 231.3
2026-08-09 | 19:00:00 | 1.8 | 18.1 | 213 | 239.02 | 2.25 | 3.43 | 215.2 | 239 | 0.8 | 0.9 | 214.5 | 237.8 | 0 | 0 | 218 | 239.3
2026-08-09 | 20:00:00 | 1.3 | 3.6 | 217.96 | 240.7 | 1.83 | 4.52 | 213.5 | 240.2 | 0.39 | 1.28 | 218.5 | 238.7 | 0 | 0 | 214.9 | 239.3
2026-08-09 | 21:00:00 | 1.2 | 4.3 | 228.69 | 240.9 | 1.51 | 2.24 | 227.8 | 240.5 | 0.28 | 0.4 | 228 | 240.7 | 0 | 0 | 227.6 | 239.3
2026-08-09 | 22:00:00 | 1.3 | 2 | 234.75 | 244.38 | 1.44 | 4.59 | 236.1 | 243.7 | 0.28 | 0.66 | 236.1 | 243.5 | 0 | 0 | 236.7 | 242.1
2026-08-09 | 23:00:00 | 1.1 | 3.1 | 227.79 | 241.4 | 1.46 | 13.26 | 226.8 | 240.4 | 0.54 | 0.58 | 230.2 | 240.6 | 0 | 0 | 230.8 | 238.7
2026-08-10 | 00:00:00 | 0.9 | 2.9 | 233.06 | 241.89 | 1.35 | 1.95 | 234.5 | 241.5 | 0.52 | 0.55 | 234.4 | 241.9 | 0 | 0 | 233.6 | 239.3
2026-08-10 | 01:00:00 | 1.1 | 3.7 | 235.34 | 242.59 | 1.34 | 6.87 | 236.3 | 241.8 | 0.52 | 0.56 | 236.9 | 241.9 | 0 | 0 | 234.2 | 239.9
2026-08-10 | 02:00:00 | 0.8 | 1.4 | 237.62 | 241.7 | 1.26 | 3.93 | 238.1 | 241.7 | 0.28 | 0.54 | 237.7 | 241.9 | 0 | 0 | 239.3 | 239.3
2026-08-10 | 03:00:00 | 0.9 | 3.5 | 233.36 | 240.9 | 1.24 | 1.65 | 235.3 | 241.2 | 0.28 | 0.3 | 235.5 | 241.1 | 0 | 0 | 231.8 | 239.3
2026-08-10 | 04:00:00 | 0.8 | 12.6 | 224.42 | 237.72 | 1.25 | 1.61 | 228.7 | 239.4 | 0.28 | 0.68 | 229 | 239.8 | 0 | 0 | 226.6 | 240.5
2026-08-10 | 05:00:00 | 0.9 | 17 | 219.35 | 241.8 | 1.39 | 13.01 | 214 | 241.3 | 0.56 | 12.05 | 214 | 240.5 | 0 | 0 | 214.2 | 240.2
2026-08-10 | 06:00:00 | 1.1 | 13.1 | 221.14 | 238.42 | 1.37 | 12.98 | 216.3 | 237.5 | 0.54 | 9.75 | 215.6 | 238 | 0 | 0 | 215.6 | 239
2026-08-10 | 07:00:00 | 0.9 | 12.5 | 223.92 | 244.68 | 1.37 | 14.19 | 220.7 | 243 | 0.54 | 9.52 | 223 | 242.5 | 0 | 0 | 220.7 | 243.8
2026-08-10 | 08:00:00 | 0.8 | 12.7 | 210.42 | 247.55 | 2.34 | 9.69 | 216.1 | 246.1 | 0.53 | 4.35 | 216.2 | 245.7 | 0 | 0 | 220.2 | 244.8
2026-08-10 | 09:00:00 | 0.9 | 10.8 | 214.59 | 249.94 | 1.81 | 6.81 | 216.6 | 247.2 | 0.3 | 0.61 | 216.8 | 249.1 | 0 | 0 | 217.9 | 248.3
2026-08-10 | 10:00:00 | 1 | 1.4 | 226.21 | 245.67 | 1.82 | 14.36 | 225.2 | 243.6 | 0.3 | 6.63 | 225.3 | 245.2 | 0 | 0 | 224.7 | 245
2026-08-10 | 11:00:00 | 1.1 | 13.3 | 218.36 | 244.48 | 2.16 | 5.27 | 224.4 | 243.4 | 0.3 | 3.18 | 224.8 | 243.5 | 0 | 0 | 222.7 | 241.1
2026-08-10 | 12:00:00 | 1.2 | 12.8 | 216.97 | 240.6 | 2.82 | 4.41 | 217.6 | 239 | 0.56 | 1.15 | 217.9 | 239.6 | 0 | 0 | 217.5 | 238.4
2026-08-10 | 13:00:00 | 1.2 | 15.3 | 211.41 | 233.65 | 2.02 | 7.73 | 212.6 | 230.3 | 0.55 | 0.62 | 213.8 | 230.3 | 0 | 0 | 213.9 | 231.7
2026-08-10 | 14:00:00 | 2.1 | 21.2 | 208.83 | 234.84 | 2.87 | 20.71 | 207.2 | 233.5 | 0.55 | 8.95 | 205.9 | 233.5 | 0 | 0 | 208.8 | 234.4
2026-08-10 | 15:00:00 | 1.7 | 21.3 | 206.44 | 235.54 | 2.76 | 20.74 | 203.1 | 233.9 | 0.55 | 1.19 | 204.7 | 234.2 | 0 | 0 | 200.5 | 234.4
2026-08-10 | 16:00:00 | 2.3 | 20.7 | 202.08 | 230.87 | 2.8 | 4.07 | 201.2 | 229.9 | 0.78 | 1.16 | 201.5 | 231.1 | 0 | 0 | 201 | 231.7
2026-08-10 | 17:00:00 | 2.6 | 18.9 | 206.15 | 237.33 | 2.62 | 4.16 | 206.7 | 237.9 | 0.6 | 0.84 | 207.6 | 236.5 | 0 | 0 | 206 | 234.7
2026-08-10 | 18:00:00 | 2.7 | 8.8 | 206.15 | 240.41 | 2.6 | 7.64 | 207.5 | 239.7 | 0.6 | 1.07 | 209 | 239.8 | 0 | 0 | 208.2 | 239
2026-08-10 | 19:00:00 | 2.4 | 29.3 | 211.71 | 237.62 | 1.96 | 3.45 | 218 | 238.6 | 0.83 | 1.39 | 217.5 | 238.5 | 0 | 0 | 215.6 | 238.7
2026-08-10 | 20:00:00 | 1.2 | 7.7 | 224.42 | 244.68 | 2.1 | 3.46 | 222.5 | 244.6 | 0.66 | 1.47 | 222.6 | 244.2 | 0 | 0 | 222.7 | 240.5
2026-08-10 | 21:00:00 | 1.2 | 2.4 | 232.96 | 244.28 | 1.73 | 3.89 | 231.4 | 244.6 | 0.52 | 0.88 | 232.4 | 244.2 | 0 | 0 | 233.9 | 240.5
2026-08-10 | 22:00:00 | 1.3 | 3.9 | 234.35 | 242.49 | 1.28 | 6.5 | 233.6 | 242.2 | 0.28 | 0.54 | 233.9 | 242.6 | 0 | 0 | 232.8 | 243.5
2026-08-10 | 23:00:00 | 1.1 | 2 | 234.15 | 241.8 | 1.26 | 1.73 | 232.9 | 241.6 | 0.29 | 0.32 | 236.6 | 241.9 | 0 | 0 | 236.1 | 243.5
2026-08-11 | 00:00:00 | 0.9 | 4 | 231.37 | 241.4 | 1.22 | 5 | 232.9 | 240.9 | 0.28 | 0.31 | 234.5 | 241.4 | 0 | 0 | 234.4 | 241.4
2026-08-11 | 01:00:00 | 1.1 | 2 | 231.87 | 241.3 | 1.24 | 4.48 | 234.6 | 241.5 | 0.28 | 0.68 | 233.3 | 241.8 | 0 | 0 | 235 | 242.9
2026-08-11 | 02:00:00 | 0.8 | 3.7 | 236.33 | 244.18 | 1.25 | 2.03 | 236.5 | 244.6 | 0.28 | 0.57 | 235.6 | 244.2 | 0 | 0 | 235 | 242
2026-08-11 | 03:00:00 | 0.8 | 3.4 | 234.65 | 244.48 | 1.22 | 1.64 | 233.6 | 244.6 | 0.28 | 0.3 | 233.6 | 244.1 | 0 | 0 | 232.9 | 241.4
2026-08-11 | 04:00:00 | 0.9 | 3.3 | 230.08 | 243.38 | 1.28 | 1.56 | 229.3 | 243.2 | 0.28 | 0.3 | 229.6 | 243.6 | 0 | 0 | 229.2 | 240.2
2026-08-11 | 05:00:00 | 0.9 | 3.8 | 224.52 | 247.36 | 1.31 | 13.91 | 225 | 246.2 | 0.29 | 11.78 | 225.2 | 246.4 | 0 | 0 | 223 | 245.3
2026-08-11 | 06:00:00 | 1.1 | 18.3 | 219.55 | 244.77 | 1.48 | 13.65 | 220 | 243.9 | 0.3 | 4.47 | 220.2 | 243.6 | 0 | 0 | 218.8 | 244.1
2026-08-11 | 07:00:00 | 0.9 | 12.4 | 227.69 | 247.46 | 1.63 | 7.99 | 228 | 246.6 | 0.29 | 0.79 | 228.1 | 246.8 | 0 | 0 | 228.2 | 247.5
2026-08-11 | 08:00:00 | 0.9 | 12.1 | 213.99 | 244.77 | 1.67 | 13.16 | 215 | 242.8 | 0.3 | 0.76 | 215.4 | 243.3 | 0 | 0 | 213.5 | 243.8
2026-08-11 | 09:00:00 | 1.1 | 3.8 | 219.35 | 250.53 | 1.82 | 7.54 | 215.3 | 251.1 | 0.55 | 0.6 | 216.6 | 250.3 | 0 | 0 | 216.5 | 246.9
2026-08-11 | 10:00:00 | 0.9 | 3.6 | 218.66 | 238.82 | 1.98 | 8.5 | 217.5 | 237.8 | 0.55 | 6.98 | 218.5 | 237.7 | 0 | 0 | 217 | 236.4
2026-08-11 | 11:00:00 | 0.9 | 12.2 | 222.23 | 240.11 | 2.09 | 3.26 | 224.7 | 238.9 | 0.79 | 0.84 | 222.1 | 239.4 | 0 | 0 | 222.4 | 239.6
2026-08-11 | 12:00:00 | 1.4 | 13.2 | 207.44 | 240.21 | 1.78 | 2.7 | 207.7 | 239.4 | 0.73 | 1.4 | 209 | 239.4 | 0 | 0 | 208.2 | 241.4
2026-08-11 | 13:00:00 | 1.8 | 7.7 | 215.38 | 229.78 | 1.68 | 10.56 | 209.8 | 228.8 | 0.59 | 9.4 | 209.4 | 228.6 | 0 | 0 | 210.2 | 229.2
2026-08-11 | 14:00:00 | 1.6 | 12.8 | 211.61 | 230.28 | 2.23 | 11.3 | 207.9 | 228.3 | 0.72 | 9.3 | 207.1 | 228.2 | 0 | 0 | 209.8 | 226.3
2026-08-11 | 15:00:00 | 2 | 13.6 | 199.99 | 231.17 | 2.74 | 15.14 | 196.5 | 230.6 | 1.37 | 11.38 | 195.7 | 230.8 | 0 | 0 | 198.1 | 229.2
2026-08-11 | 16:00:00 | 2.5 | 19.9 | 190.85 | 234.05 | 4.48 | 9.64 | 192 | 231.2 | 1.38 | 2.32 | 191.8 | 231.8 | 0 | 0 | 192.6 | 232.5
2026-08-11 | 17:00:00 | 8.5 | 19.9 | 193.24 | 227.69 | 4.81 | 15.69 | 195.6 | 227 | 1.72 | 1.93 | 196.7 | 227.5 | 0 | 0 | 197.7 | 227.4
2026-08-11 | 18:00:00 | 8.1 | 14.6 | 216.37 | 231.96 | 3.69 | 5.24 | 218.2 | 233.2 | 1.21 | 1.78 | 218.5 | 233.3 | 0 | 0 | 218.7 | 232
2026-08-11 | 19:00:00 | 3 | 27.2 | 211.21 | 232.36 | 3.24 | 4.7 | 217.1 | 232.9 | 1.15 | 2.25 | 217.1 | 232.9 | 0 | 0 | 220.9 | 232.3
2026-08-11 | 20:00:00 | 1.9 | 18.9 | 214.79 | 238.52 | 1.88 | 4.07 | 217.8 | 237.6 | 0.64 | 1.73 | 217.8 | 237.9 | 0 | 0 | 217.3 | 237.3
2026-08-11 | 21:00:00 | 1.8 | 4.4 | 233.36 | 241.2 | 1.76 | 6.66 | 233.7 | 240.7 | 0.53 | 0.64 | 233.8 | 240.7 | 0 | 0 | 235.6 | 241.4
2026-08-11 | 22:00:00 | 1.7 | 3.8 | 230.87 | 241.1 | 1.38 | 2.28 | 230.6 | 241 | 0.52 | 0.55 | 231.1 | 241.3 | 0 | 0 | 229 | 239.3
2026-08-11 | 23:00:00 | 1.2 | 4.3 | 233.26 | 246.36 | 1.4 | 6.2 | 233.9 | 246 | 0.52 | 0.54 | 232.8 | 246 | 0 | 0 | 233.6 | 240.9
2026-08-12 | 00:00:00 | 1.2 | 2 | 233.06 | 242.79 | 1.36 | 1.73 | 236 | 242.6 | 0.29 | 0.54 | 235 | 242.6 | 0 | 0 | 235 | 242
2026-08-12 | 01:00:00 | 1.4 | 4.2 | 227.5 | 237.62 | 1.24 | 1.73 | 231.2 | 239.3 | 0.28 | 0.3 | 231.8 | 239.4 | 0 | 0 | 231.4 | 238.2
2026-08-12 | 02:00:00 | 1.2 | 1.9 | 233.26 | 241.3 | 1.24 | 2.22 | 234.7 | 240.7 | 0.28 | 0.3 | 233.6 | 240.9 | 0 | 0 | 231.1 | 238.6
2026-08-12 | 03:00:00 | 1.2 | 1.6 | 231.96 | 239.81 | 1.24 | 2.05 | 232.1 | 240.1 | 0.29 | 8.65 | 232.3 | 239.6 | 0 | 0 | 231.9 | 238.6
2026-08-12 | 04:00:00 | 1.2 | 3.9 | 229.68 | 242.69 | 1.39 | 6.4 | 228.5 | 242.6 | 0.53 | 0.59 | 229 | 242.6 | 0 | 0 | 228.4 | 239.9
2026-08-12 | 05:00:00 | 1.2 | 13.1 | 223.52 | 246.26 | 1.38 | 12.47 | 220.2 | 245.9 | 0.53 | 12.08 | 220.1 | 245.7 | 0 | 0 | 219 | 244.7
2026-08-12 | 06:00:00 | 1.1 | 13.2 | 220.55 | 239.61 | 1.39 | 2.43 | 217.7 | 239.2 | 0.53 | 1.34 | 218 | 239 | 0 | 0 | 217.7 | 238.7
2026-08-12 | 07:00:00 | 1.5 | 20.5 | 213.1 | 240.41 | 2.03 | 14.12 | 212.7 | 239.3 | 0.35 | 9.17 | 212.2 | 238.9 | 0 | 0 | 211.4 | 239.9
2026-08-12 | 08:00:00 | 1.2 | 16.7 | 214.09 | 241.1 | 1.92 | 13.56 | 210.8 | 240.4 | 0.32 | 3.88 | 210.9 | 240.3 | 0 | 0 | 210.9 | 240.7
2026-08-12 | 09:00:00 | 1.1 | 12 | 214.19 | 244.28 | 2.14 | 11.34 | 217.7 | 242.3 | 0.31 | 9.21 | 215.8 | 242.8 | 0 | 0 | 215.3 | 242.9
2026-08-12 | 10:00:00 | 1.1 | 13 | 213.89 | 238.22 | 2.88 | 11.42 | 214.5 | 237.8 | 0.6 | 9.15 | 215.8 | 236.9 | 0 | 0 | 215.3 | 238.2
2026-08-12 | 11:00:00 | 1.7 | 10.5 | 213 | 235.54 | 3.02 | 6.45 | 209.8 | 233.4 | 0.59 | 2 | 210 | 233.9 | 0 | 0 | 213.7 | 234.6
2026-08-12 | 12:00:00 | 1.7 | 8.3 | 217.57 | 232.56 | 4.01 | 9.11 | 215.2 | 230.3 | 1.51 | 2.05 | 215.3 | 229.9 | 0 | 0 | 217.7 | 229.9
2026-08-12 | 13:00:00 | 1.7 | 2.7 | 215.48 | 231.47 | 3.44 | 6.36 | 215.1 | 228.6 | 1.4 | 3.37 | 214.8 | 228.7 | 0 | 0 | 218.8 | 230.3
2026-08-12 | 14:00:00 | 2 | 2.9 | 211.51 | 227.99 | 4.01 | 6.87 | 210.3 | 226.8 | 1.26 | 2.08 | 210.7 | 226.6 | 0 | 0 | 212.5 | 227.1
2026-08-12 | 15:00:00 | 1.9 | 4.5 | 211.81 | 228.09 | 4.57 | 13.67 | 206.7 | 224.5 | 1.84 | 10.87 | 205.4 | 224.4 | 0 | 0 | 209.3 | 224.2
2026-08-12 | 16:00:00 | 1.7 | 7.8 | 204.16 | 224.02 | 4.61 | 6.21 | 202.2 | 220.7 | 1.83 | 2.15 | 201.7 | 220.7 | 0 | 0 | 201.6 | 221.4
2026-08-12 | 17:00:00 | 7.7 | 20.6 | 187.78 | 220.35 | 4.17 | 10.34 | 188.8 | 219.9 | 1.54 | 2.15 | 189.5 | 219.4 | 0 | 0 | 189.4 | 221.9
2026-08-12 | 18:00:00 | 8.6 | 10 | 204.56 | 223.03 | 3.77 | 9.02 | 206 | 223.4 | 1.5 | 2.09 | 205.7 | 222.9 | 0 | 0 | 205 | 222.4
2026-08-12 | 19:00:00 | 8.1 | 19.5 | 205.05 | 224.52 | 3.55 | 8.45 | 206.6 | 224.3 | 1.44 | 2.29 | 206.9 | 224.4 | 0 | 0 | 207.8 | 223.5
2026-08-12 | 20:00:00 | 2.6 | 20.5 | 204.96 | 231.17 | 2.86 | 4.34 | 206.4 | 232.5 | 0.99 | 2.01 | 206.6 | 232.4 | 0 | 0 | 208.9 | 229
2026-08-12 | 21:00:00 | 2.1 | 5 | 221.74 | 236.14 | 2.18 | 6.28 | 221.4 | 235.8 | 0.56 | 1.52 | 222.9 | 235.6 | 0 | 0 | 221.8 | 233.3
2026-08-12 | 22:00:00 | 1.6 | 2.2 | 223.43 | 237.13 | 2.04 | 5.26 | 221.5 | 236.9 | 0.55 | 0.58 | 222.4 | 236.6 | 0 | 0 | 221.9 | 235.3
2026-08-12 | 23:00:00 | 1.5 | 3.2 | 233.36 | 239.02 | 1.76 | 2.57 | 233.5 | 238.6 | 0.54 | 0.56 | 233.5 | 238.5 | 0 | 0 | 235.3 | 237.3
2026-08-13 | 00:00:00 | 1.5 | 2 | 234.45 | 240.5 | 1.77 | 3.6 | 235.7 | 240 | 0.54 | 0.56 | 234.5 | 240.1 | 0 | 0 | 236.6 | 237.9
2026-08-13 | 01:00:00 | 1.1 | 1.6 | 236.53 | 240.6 | 1.7 | 2.42 | 236.1 | 240.2 | 0.54 | 0.56 | 235.9 | 240.5 | 0 | 0 | 236.6 | 238.2
2026-08-13 | 02:00:00 | 0.9 | 1.8 | 235.54 | 243.78 | 1.37 | 2.4 | 234.9 | 243.7 | 0.54 | 0.56 | 236.1 | 242.8 | 0 | 0 | 236.7 | 238.7
2026-08-13 | 03:00:00 | 1.1 | 3.5 | 234.05 | 239.11 | 1.28 | 6.65 | 233.6 | 238.9 | 0.28 | 0.55 | 234.7 | 239.3 | 0 | 0 | 235.6 | 237.3
2026-08-13 | 04:00:00 | 0.9 | 3.5 | 220.35 | 241.1 | 1.27 | 1.59 | 217.8 | 240.4 | 0.28 | 0.3 | 218.8 | 240.8 | 0 | 0 | 218.2 | 237.9
2026-08-13 | 05:00:00 | 1.2 | 4.3 | 217.37 | 241.89 | 1.29 | 12.69 | 216.7 | 242.4 | 0.28 | 11.43 | 217 | 242.5 | 0 | 0 | 217.3 | 241.3
2026-08-13 | 06:00:00 | 1.2 | 13.1 | 215.68 | 243.09 | 1.3 | 12.93 | 213.2 | 241.5 | 0.3 | 2.04 | 213.4 | 241.6 | 0 | 0 | 210.7 | 242.3
2026-08-13 | 07:00:00 | 1.2 | 19.1 | 213.79 | 239.51 | 3.1 | 18.43 | 212.2 | 238 | 0.6 | 4.99 | 214 | 238.6 | 0 | 0 | 210.9 | 239
2026-08-13 | 08:00:00 | 1.5 | 12.9 | 213.99 | 233.75 | 2.69 | 7.69 | 212.6 | 233.5 | 0.56 | 0.64 | 213.6 | 233.8 | 0 | 0 | 212.6 | 235
2026-08-13 | 09:00:00 | 1.4 | 13.3 | 219.35 | 236.83 | 3.17 | 7.34 | 217.3 | 235.2 | 0.56 | 1.57 | 217.5 | 235.4 | 0 | 0 | 216.1 | 234.4
2026-08-13 | 10:00:00 | 1.4 | 13 | 213 | 234.25 | 3.82 | 10.86 | 212.8 | 231.5 | 1.45 | 7.61 | 212 | 232.2 | 0 | 0 | 210.7 | 232.5
2026-08-13 | 11:00:00 | 1.4 | 1.8 | 215.08 | 232.36 | 4.47 | 5.68 | 215.7 | 229.5 | 1.44 | 2.01 | 215.3 | 229.8 | 0 | 0 | 215.9 | 227.9
2026-08-13 | 12:00:00 | 1.4 | 4 | 220.35 | 233.85 | 3.22 | 5.92 | 221 | 231.2 | 1.52 | 2.01 | 221.1 | 230.8 | 0 | 0 | 222.4 | 230.3
2026-08-13 | 13:00:00 | 1.4 | 13.3 | 209.92 | 233.06 | 2.9 | 5.97 | 211.1 | 230.9 | 1.45 | 1.52 | 212.5 | 230.8 | 0 | 0 | 211.8 | 231.4
2026-08-13 | 14:00:00 | 2.6 | 17.3 | 214.59 | 229.18 | 4.46 | 16.25 | 215.4 | 228.2 | 1.45 | 2.03 | 215.5 | 228.2 | 0 | 0 | 217.3 | 225.3
2026-08-13 | 15:00:00 | 8.3 | 21.2 | 202.67 | 227.69 | 4.57 | 9.18 | 199.1 | 226.5 | 1.99 | 2.09 | 199.4 | 225.8 | 0 | 0 | 201.6 | 225
2026-08-13 | 16:00:00 | 8.3 | 28.4 | 196.81 | 217.67 | 4.82 | 19.51 | 193 | 215.3 | 2 | 2.49 | 194.4 | 215.3 | 0 | 0 | 192.6 | 215.8
2026-08-13 | 17:00:00 | 7.9 | 23.7 | 200.49 | 226.6 | 3.11 | 12.27 | 198.8 | 224.4 | 1.47 | 2.05 | 198.5 | 224.9 | 0 | 0 | 202.4 | 225.7
2026-08-13 | 18:00:00 | 7.8 | 24.3 | 204.86 | 232.66 | 2.44 | 6.27 | 209.4 | 233.6 | 0.87 | 2.04 | 208.4 | 233.4 | 0 | 0 | 208.7 | 233.6
2026-08-13 | 19:00:00 | 7.3 | 19.5 | 216.77 | 231.77 | 1.97 | 3.29 | 218.6 | 232.6 | 0.83 | 1.13 | 218.9 | 233 | 0 | 0 | 217.3 | 232.2
2026-08-13 | 20:00:00 | 2.2 | 13.2 | 224.22 | 239.31 | 1.98 | 2.9 | 227.5 | 239.2 | 0.81 | 1.42 | 227.7 | 239.9 | 0 | 0 | 227.6 | 239.9
2026-08-13 | 21:00:00 | 1.6 | 3.2 | 228.89 | 242.69 | 1.89 | 2.61 | 227.5 | 242.6 | 0.54 | 1.07 | 227.9 | 242.6 | 0 | 0 | 227.1 | 242.6
2026-08-13 | 22:00:00 | 1.4 | 3.9 | 233.85 | 241.3 | 1.38 | 2.46 | 233.8 | 241.1 | 0.53 | 0.54 | 234 | 241.1 | 0 | 0 | 235.3 | 238.7
2026-08-13 | 23:00:00 | 1.3 | 2.3 | 230.87 | 240.6 | 1.45 | 6.7 | 233 | 239.4 | 0.52 | 0.54 | 232 | 239.8 | 0 | 0 | 230 | 237.3
2026-08-14 | 00:00:00 | 1.4 | 3.1 | 232.56 | 241.2 | 1.42 | 6.06 | 234.8 | 241.1 | 0.52 | 0.54 | 234.3 | 241.3 | 0 | 0 | 236.7 | 239.3
2026-08-14 | 01:00:00 | 1.2 | 4 | 236.73 | 241.1 | 1.35 | 4.51 | 237.2 | 240.6 | 0.52 | 0.54 | 237.6 | 240.6 | 0 | 0 | 238.7 | 239.6
2026-08-14 | 02:00:00 | 1.1 | 3.9 | 238.02 | 242.79 | 1.39 | 4.87 | 238.5 | 242.5 | 0.52 | 0.53 | 238.1 | 243 | 0 | 0 | 239.3 | 241.1
2026-08-14 | 03:00:00 | 0.8 | 1.7 | 239.31 | 243.48 | 1.26 | 1.73 | 239.2 | 243 | 0.28 | 0.53 | 239.3 | 243.3 | 0 | 0 | 241.1 | 241.5
2026-08-14 | 04:00:00 | 0.9 | 1.7 | 235.54 | 244.28 | 1.25 | 1.73 | 235.4 | 244.2 | 0.28 | 0.3 | 235.7 | 243.7 | 0 | 0 | 236.1 | 242.3
2026-08-14 | 05:00:00 | 1.3 | 4.1 | 225.61 | 245.87 | 1.26 | 13.17 | 222.5 | 245.7 | 0.28 | 11.75 | 222.9 | 245.4 | 0 | 0 | 223.2 | 245.6
2026-08-14 | 06:00:00 | 1.2 | 13.9 | 224.02 | 245.57 | 2.69 | 14.78 | 222.2 | 244.3 | 0.59 | 1.2 | 222.7 | 244.6 | 0 | 0 | 223 | 240.4
2026-08-14 | 07:00:00 | 1.2 | 12.8 | 217.57 | 239.41 | 2.57 | 14.11 | 217.5 | 238.4 | 0.54 | 4.63 | 216.4 | 238.6 | 0 | 0 | 216.6 | 238.4
2026-08-14 | 08:00:00 | 1.5 | 13.8 | 219.35 | 240.7 | 2.81 | 10.02 | 222.3 | 239.3 | 0.53 | 0.59 | 222.4 | 239.7 | 0 | 0 | 223.5 | 238.4
2026-08-14 | 09:00:00 | 1.5 | 13.6 | 215.38 | 245.77 | 2.79 | 4.51 | 217.4 | 244.3 | 0.52 | 0.58 | 217.7 | 245.7 | 0 | 0 | 217 | 242.9
2026-08-14 | 10:00:00 | 1.8 | 14.3 | 219.25 | 240.9 | 1.5 | 8.27 | 223.3 | 239.8 | 0.53 | 6.85 | 222.8 | 240.1 | 0 | 0 | 222.4 | 241
2026-08-14 | 11:00:00 | 1.1 | 17.1 | 219.85 | 242.29 | 1.46 | 2.81 | 225.8 | 243.4 | 0.52 | 1.09 | 225.7 | 243.9 | 0 | 0 | 223.5 | 241.1
2026-08-14 | 12:00:00 | 1.6 | 11.5 | 216.67 | 239.81 | 2.64 | 10.24 | 220.9 | 238.4 | 1.04 | 1.11 | 220.5 | 238.6 | 0 | 0 | 218.8 | 238.2
2026-08-14 | 13:00:00 | 1.4 | 11 | 222.03 | 238.62 | 2.75 | 9.45 | 221.8 | 237.1 | 0.3 | 1.06 | 221.9 | 237.8 | 0 | 0 | 221.9 | 238.2
2026-08-14 | 14:00:00 | 1.3 | 13.4 | 222.13 | 238.32 | 2.43 | 12.85 | 222.9 | 236.7 | 0.3 | 10.36 | 221.3 | 237.1 | 0 | 0 | 222.4 | 237.4
2026-08-14 | 15:00:00 | 1.4 | 4.2 | 215.68 | 236.33 | 2.62 | 11.18 | 211.5 | 234.8 | 0.65 | 7.52 | 210.9 | 234.6 | 0 | 0 | 211.8 | 233.9
2026-08-14 | 16:00:00 | 2.2 | 20.3 | 200.98 | 229.28 | 3.96 | 15.52 | 199.3 | 227.5 | 1.15 | 2.22 | 199.6 | 227.5 | 0 | 0 | 199.3 | 227.3
2026-08-14 | 17:00:00 | 7.1 | 20.4 | 210.22 | 241.89 | 2.72 | 9.07 | 211.2 | 240.5 | 0.96 | 1.25 | 212.5 | 242.2 | 0 | 0 | 213 | 240.5
2026-08-14 | 18:00:00 | 7.2 | 18.7 | 214.98 | 240.5 | 2.05 | 3.8 | 216.9 | 240.8 | 0.62 | 1.02 | 217.3 | 241.4 | 0 | 0 | 217 | 240.8
2026-08-14 | 19:00:00 | 1.6 | 13.5 | 220.94 | 239.11 | 1.54 | 6.36 | 220.2 | 238.8 | 0.56 | 0.8 | 220.6 | 238.3 | 0 | 0 | 219.2 | 237.9
2026-08-14 | 20:00:00 | 2.4 | 4.3 | 222.13 | 237.53 | 1.54 | 8.21 | 222.8 | 237.3 | 0.57 | 1.28 | 222.9 | 238.1 | 0 | 0 | 225.3 | 236.7
2026-08-14 | 21:00:00 | 1.8 | 2.9 | 231.96 | 240.6 | 1.69 | 2.55 | 232.7 | 240.5 | 0.41 | 0.81 | 231.3 | 240.6 | 0 | 0 | 231.1 | 236.7
2026-08-14 | 22:00:00 | 1.3 | 4.2 | 231.87 | 241.7 | 1.48 | 3.48 | 231.1 | 240.6 | 0.54 | 0.59 | 231.2 | 240.7 | 0 | 0 | 230.9 | 239.6
2026-08-14 | 23:00:00 | 1.3 | 4.1 | 233.65 | 240.5 | 1.39 | 5.75 | 234.9 | 241.1 | 0.53 | 0.55 | 231.6 | 240.4 | 0 | 0 | 235.9 | 237.9
2026-08-15 | 00:00:00 | 1 | 1.7 | 237.03 | 241 | 1.34 | 3.86 | 236.7 | 240.9 | 0.53 | 0.54 | 236.9 | 240.9 | 0 | 0 | 236.2 | 239.9
2026-08-15 | 01:00:00 | 1 | 3.7 | 238.12 | 242.29 | 1.33 | 2.05 | 237.8 | 241.9 | 0.53 | 0.54 | 237.6 | 242.6 | 0 | 0 | 236.2 | 238.7
2026-08-15 | 02:00:00 | 0.9 | 2.2 | 238.92 | 241.99 | 1.34 | 5.93 | 239.4 | 241.9 | 0.52 | 0.53 | 239.2 | 242.2 | 0 | 0 | 238.7 | 240.5
2026-08-15 | 03:00:00 | 1.1 | 2.3 | 238.92 | 243.29 | 1.38 | 1.95 | 238.4 | 242.6 | 0.52 | 0.54 | 238.1 | 242.7 | 0 | 0 | 238.4 | 241.1
2026-08-15 | 04:00:00 | 1.1 | 3.4 | 236.14 | 243.98 | 1.28 | 1.63 | 236.1 | 243.8 | 0.28 | 0.52 | 236.2 | 243.9 | 0 | 0 | 236.1 | 242
2026-08-15 | 05:00:00 | 1 | 12.3 | 230.08 | 244.08 | 1.46 | 13.32 | 228.9 | 244.5 | 0.28 | 12.4 | 229.1 | 243.9 | 0 | 0 | 229.5 | 241.7
2026-08-15 | 06:00:00 | 1.2 | 12.8 | 217.96 | 241.1 | 1.31 | 18.59 | 220 | 240.5 | 0.3 | 6.86 | 220.4 | 240.9 | 0 | 0 | 218.5 | 240.5
2026-08-15 | 07:00:00 | 1 | 13 | 218.86 | 241.1 | 2.07 | 13.98 | 217.5 | 240.3 | 0.62 | 5.03 | 217.8 | 240.2 | 0 | 0 | 218.3 | 240.5
2026-08-15 | 08:00:00 | 1.5 | 12.9 | 217.67 | 250.34 | 1.59 | 7.13 | 216.6 | 248.9 | 0.7 | 0.8 | 216.3 | 248.9 | 0 | 0 | 215.1 | 246.6
2026-08-15 | 09:00:00 | 1 | 26 | 213.59 | 245.07 | 1.89 | 14.04 | 217.1 | 243.9 | 0.71 | 11.99 | 215.5 | 244.1 | 0 | 0 | 218.3 | 244.4
2026-08-15 | 10:00:00 | 1.1 | 12.7 | 223.52 | 244.77 | 1.9 | 14.08 | 225.4 | 244.1 | 0.7 | 0.72 | 225.5 | 243.4 | 0 | 0 | 227.4 | 244
2026-08-15 | 11:00:00 | 1.6 | 2.3 | 225.01 | 239.41 | 1.55 | 2.52 | 222.5 | 239.1 | 0.55 | 0.75 | 222.8 | 239.3 | 0 | 0 | 227.1 | 237.6
2026-08-15 | 12:00:00 | 1.1 | 4.1 | 231.67 | 243.48 | 1.3 | 1.8 | 230 | 242.5 | 0.33 | 0.57 | 230.3 | 243.4 | 0 | 0 | 229.8 | 243.5
2026-08-15 | 13:00:00 | 1.2 | 10.7 | 227.1 | 243.19 | 1.3 | 1.9 | 229.6 | 242.6 | 0.33 | 0.35 | 228.2 | 242.7 | 0 | 0 | 231.7 | 240.5
2026-08-15 | 14:00:00 | 1.7 | 13.4 | 212.3 | 238.42 | 1.39 | 2.08 | 213.5 | 237.3 | 0.34 | 1.12 | 214 | 237.4 | 0 | 0 | 212.3 | 237.6
2026-08-15 | 15:00:00 | 1.5 | 18.1 | 212.3 | 238.32 | 1.51 | 17.93 | 208.3 | 237 | 0.58 | 17.12 | 206.9 | 237.4 | 0 | 0 | 206.5 | 236.7
2026-08-15 | 16:00:00 | 7.5 | 34.2 | 202.87 | 233.75 | 1.39 | 4.74 | 210.4 | 233.8 | 0.56 | 0.63 | 212.2 | 234.2 | 0 | 0 | 209.9 | 230.6
2026-08-15 | 17:00:00 | 7.4 | 14.5 | 216.28 | 236.14 | 1.73 | 3.34 | 218 | 236.2 | 0.55 | 0.62 | 217.8 | 236.3 | 0 | 0 | 220.2 | 237
2026-08-15 | 18:00:00 | 2.6 | 18.6 | 214.29 | 237.43 | 1.85 | 3.27 | 216.4 | 237.1 | 0.55 | 1.13 | 217 | 237 | 0 | 0 | 219.2 | 237.5
2026-08-15 | 19:00:00 | 1.6 | 18.4 | 224.52 | 241.2 | 1.79 | 3.93 | 226.1 | 240.7 | 0.77 | 0.88 | 226.1 | 240.8 | 0 | 0 | 226 | 238.4
2026-08-15 | 20:00:00 | 1.9 | 2.9 | 231.96 | 240.8 | 2.23 | 7.49 | 230.3 | 240.2 | 0.82 | 2.84 | 230 | 240.4 | 0 | 0 | 231 | 238.4
2026-08-15 | 21:00:00 | 1.6 | 3.1 | 230.48 | 242.79 | 1.87 | 2.71 | 230.5 | 242 | 0.53 | 1.39 | 231.4 | 242.4 | 0 | 0 | 231 | 242.6
2026-08-15 | 22:00:00 | 1.4 | 4 | 234.35 | 242.49 | 1.45 | 2.47 | 235.6 | 242.3 | 0.52 | 0.54 | 234.1 | 242.6 | 0 | 0 | 235 | 242.6
2026-08-15 | 23:00:00 | 1 | 1.7 | 237.23 | 246.96 | 1.4 | 1.83 | 236.5 | 246.2 | 0.51 | 0.53 | 236.4 | 246.7 | 0 | 0 | 235.6 | 242.6
2026-08-16 | 00:00:00 | 1 | 3.6 | 238.42 | 243.78 | 1.4 | 1.86 | 238.8 | 243.8 | 0.51 | 0.53 | 239.3 | 244 | 0 | 0 | 240.8 | 241.4
2026-08-16 | 01:00:00 | 0.8 | 3.4 | 236.83 | 244.68 | 1.27 | 1.95 | 237.9 | 243.3 | 0.28 | 0.52 | 237.4 | 243.5 | 0 | 0 | 235.6 | 242
2026-08-16 | 02:00:00 | 1 | 4 | 237.13 | 241.3 | 1.24 | 4.47 | 236.7 | 240.8 | 0.29 | 0.3 | 236.8 | 241.2 | 0 | 0 | 234.4 | 240.8
2026-08-16 | 03:00:00 | 1.1 | 2.7 | 236.43 | 241.2 | 1.27 | 4.11 | 236.1 | 241.7 | 0.28 | 0.69 | 235.7 | 240.9 | 0 | 0 | 234.4 | 239.9
2026-08-16 | 04:00:00 | 0.9 | 1.5 | 231.17 | 241.5 | 1.48 | 5.96 | 233.1 | 242 | 0.53 | 0.58 | 233.5 | 241.3 | 0 | 0 | 233 | 239.7
2026-08-16 | 05:00:00 | 0.9 | 13 | 221.84 | 240.7 | 1.38 | 12.25 | 225.9 | 240.3 | 0.53 | 11.83 | 224.8 | 240.6 | 0 | 0 | 220.9 | 239.3
2026-08-16 | 06:00:00 | 1 | 12.3 | 222.23 | 240.21 | 1.57 | 13.38 | 224.2 | 239.7 | 0.53 | 6.91 | 224.3 | 239.7 | 0 | 0 | 222.7 | 239.3
2026-08-16 | 07:00:00 | 1.1 | 12.5 | 211.81 | 242.19 | 1.75 | 13.11 | 211.7 | 241.2 | 0.52 | 11.83 | 212.5 | 241.6 | 0 | 0 | 212.5 | 241.1
2026-08-16 | 08:00:00 | 1.2 | 32.4 | 202.17 | 242.79 | 1.88 | 11.14 | 209.6 | 241.8 | 0.54 | 9.82 | 209.5 | 241.4 | 0 | 0 | 210.4 | 243.8
2026-08-16 | 09:00:00 | 1.1 | 23 | 215.88 | 247.06 | 1.63 | 4.07 | 221.7 | 245.7 | 0.32 | 3.98 | 221 | 246.4 | 0 | 0 | 222.4 | 246.9
2026-08-16 | 10:00:00 | 1.4 | 14.3 | 216.28 | 246.07 | 1.6 | 9.1 | 212.9 | 245.9 | 0.34 | 7.66 | 214.8 | 246 | 0 | 0 | 215.8 | 242.3
2026-08-16 | 11:00:00 | 1.6 | 14.9 | 214.79 | 244.77 | 1.7 | 8.05 | 214 | 242.8 | 0.4 | 1.22 | 214.1 | 243 | 0 | 0 | 212.8 | 244.4
2026-08-16 | 12:00:00 | 1.3 | 17.7 | 217.57 | 242.89 | 1.69 | 2.72 | 221.8 | 240.7 | 0.57 | 1.23 | 222.7 | 240.9 | 0 | 0 | 220.2 | 242.9
2026-08-16 | 13:00:00 | 1.7 | 30.1 | 204.16 | 239.51 | 1.57 | 12.66 | 211.5 | 239 | 0.56 | 11.92 | 211.3 | 239.8 | 0 | 0 | 211.4 | 237.5
2026-08-16 | 14:00:00 | 1.7 | 10.1 | 217.67 | 242.19 | 1.68 | 5.93 | 217.1 | 241.6 | 0.33 | 0.58 | 216.6 | 242.1 | 0 | 0 | 219.7 | 241.7
2026-08-16 | 15:00:00 | 1.5 | 13.2 | 215.38 | 241.99 | 1.68 | 8.25 | 216.2 | 241.2 | 0.34 | 7.45 | 216.9 | 241.5 | 0 | 0 | 219.5 | 241.7
2026-08-16 | 16:00:00 | 1.5 | 19.9 | 207.93 | 239.21 | 2.21 | 7.58 | 208.3 | 240.8 | 0.62 | 1.32 | 211.8 | 237.8 | 0 | 0 | 213.5 | 238.4
2026-08-16 | 17:00:00 | 2.6 | 15.8 | 210.02 | 236.14 | 2.09 | 3.32 | 213.1 | 234.7 | 0.6 | 1.19 | 212.5 | 236.5 | 0 | 0 | 211.2 | 237.3
2026-08-16 | 18:00:00 | 1.8 | 28.7 | 211.71 | 239.11 | 1.92 | 2.94 | 218 | 241 | 0.87 | 1.12 | 217.7 | 240.5 | 0 | 0 | 218.9 | 237.2
2026-08-16 | 19:00:00 | 1.7 | 18.6 | 218.96 | 239.81 | 2.06 | 2.9 | 224 | 238.3 | 0.85 | 1.16 | 224.1 | 239.6 | 0 | 0 | 224.5 | 237.3
2026-08-16 | 20:00:00 | 1.9 | 3.5 | 226.6 | 239.51 | 2.09 | 2.84 | 228.6 | 239.4 | 0.66 | 1.49 | 226.9 | 239.6 | 0 | 0 | 230 | 236.7
2026-08-16 | 21:00:00 | 1.1 | 1.9 | 230.97 | 244.97 | 1.85 | 2.44 | 230.9 | 244 | 0.54 | 0.77 | 230.8 | 244.1 | 0 | 0 | 230.7 | 244.4
2026-08-16 | 22:00:00 | 1.1 | 2 | 230.48 | 240.9 | 1.41 | 1.94 | 230.5 | 240.5 | 0.52 | 0.55 | 230.7 | 241 | 0 | 0 | 232.5 | 239.3
2026-08-16 | 23:00:00 | 0.9 | 3.6 | 236.63 | 240.6 | 1.29 | 3.92 | 236.4 | 240 | 0.29 | 0.53 | 236.7 | 240.3 | 0 | 0 | 237.6 | 238.4
2026-08-17 | 00:00:00 | 1.1 | 2.1 | 236.33 | 241.4 | 1.25 | 1.69 | 236.4 | 241.1 | 0.28 | 0.3 | 236.7 | 241.1 | 0 | 0 | 238.4 | 239.9
2026-08-17 | 01:00:00 | 1 | 1.8 | 238.42 | 243.68 | 1.21 | 1.61 | 236.7 | 243.9 | 0.29 | 0.3 | 238.1 | 243.9 | 0 | 0 | 233.9 | 241.7
2026-08-17 | 02:00:00 | 0.8 | 1.6 | 236.04 | 244.28 | 1.36 | 2.01 | 236.1 | 243.6 | 0.29 | 0.7 | 236.3 | 243.8 | 0 | 0 | 236.5 | 241.7
2026-08-17 | 03:00:00 | 1 | 4.3 | 235.94 | 241.6 | 1.34 | 1.9 | 235.3 | 241.6 | 0.54 | 0.57 | 235.9 | 241.4 | 0 | 0 | 235.9 | 242
2026-08-17 | 04:00:00 | 0.8 | 13.1 | 231.77 | 249.04 | 1.24 | 1.74 | 234.4 | 249.1 | 0.28 | 0.55 | 234.7 | 249.6 | 0 | 0 | 234.6 | 247.7
2026-08-17 | 05:00:00 | 1.2 | 15 | 220.35 | 241.8 | 1.43 | 12.91 | 220.9 | 241.8 | 0.32 | 12.46 | 221.1 | 241.9 | 0 | 0 | 222.3 | 240.5
2026-08-17 | 06:00:00 | 1.3 | 12.6 | 223.33 | 240.11 | 1.73 | 13.25 | 223.2 | 239.4 | 0.33 | 4.95 | 223.6 | 240.1 | 0 | 0 | 224.1 | 239.9
2026-08-17 | 07:00:00 | 1 | 12.8 | 215.78 | 247.26 | 1.61 | 13.48 | 220.8 | 246.7 | 0.58 | 4.74 | 220.7 | 246.9 | 0 | 0 | 221.4 | 243.8
2026-08-17 | 08:00:00 | 0.9 | 12.9 | 212.01 | 243.19 | 1.84 | 7.11 | 214.1 | 241.8 | 0.53 | 0.78 | 213.5 | 241.6 | 0 | 0 | 212.3 | 241.1
2026-08-17 | 09:00:00 | 0.9 | 5.7 | 226.9 | 251.63 | 1.72 | 2.81 | 226.4 | 250.2 | 0.51 | 0.55 | 226.8 | 250.2 | 0 | 0 | 225.3 | 247.2
2026-08-17 | 10:00:00 | 0.9 | 7.2 | 207.14 | 245.17 | 1.85 | 10.54 | 210.7 | 241.1 | 0.52 | 6.94 | 213.1 | 244.8 | 0 | 0 | 212.3 | 245.9
2026-08-17 | 11:00:00 | 0.9 | 3 | 218.46 | 242.09 | 1.92 | 5.9 | 223.1 | 241.1 | 0.52 | 0.55 | 223.8 | 241.2 | 0 | 0 | 222.4 | 240.5
2026-08-17 | 12:00:00 | 1 | 12.9 | 222.63 | 243.09 | 1.66 | 2.68 | 224.5 | 243.1 | 0.3 | 0.67 | 225.2 | 243.2 | 0 | 0 | 223.5 | 241.1
2026-08-17 | 13:00:00 | 1.3 | 10.6 | 223.43 | 243.09 | 1.59 | 6.26 | 225 | 242.3 | 0.29 | 0.32 | 224.5 | 242.3 | 0 | 0 | 220.7 | 242.3
2026-08-17 | 14:00:00 | 1.2 | 12.9 | 224.02 | 244.87 | 1.56 | 10.01 | 225.6 | 243.7 | 0.3 | 1.13 | 225.3 | 243.9 | 0 | 0 | 223.7 | 243.8
2026-08-17 | 15:00:00 | 1.4 | 3.9 | 220.64 | 243.29 | 2.33 | 10.11 | 218.1 | 242.4 | 0.9 | 1.25 | 218.5 | 242.9 | 0 | 0 | 217.7 | 242.6
2026-08-17 | 16:00:00 | 1.3 | 20.1 | 203.47 | 243.29 | 2.05 | 5.14 | 208.8 | 242.7 | 0.9 | 1.17 | 209.1 | 242.6 | 0 | 0 | 211.3 | 241.7
2026-08-17 | 17:00:00 | 1.5 | 28.2 | 201.78 | 239.91 | 1.78 | 2.35 | 208.6 | 239 | 0.87 | 1.14 | 208.1 | 238.9 | 0 | 0 | 211.3 | 237.9
2026-08-17 | 18:00:00 | 2.4 | 21.7 | 216.87 | 239.91 | 1.58 | 2.33 | 216.7 | 239.5 | 0.8 | 0.96 | 219.9 | 239.9 | 0 | 0 | 216.8 | 238.2
2026-08-17 | 19:00:00 | 1.9 | 18.6 | 222.13 | 242.99 | 1.58 | 2.54 | 223.6 | 241.8 | 0.78 | 1.42 | 223.6 | 241.9 | 0 | 0 | 224.2 | 241.3
2026-08-17 | 20:00:00 | 2.2 | 18.3 | 218.56 | 239.31 | 2.05 | 13.57 | 213.8 | 236.1 | 0.66 | 1.49 | 217.9 | 236.1 | 0 | 0 | 213 | 236.6
2026-08-17 | 21:00:00 | 1.4 | 3.6 | 222.63 | 238.02 | 2.11 | 13.21 | 218.2 | 235.7 | 0.54 | 0.67 | 218.2 | 236.2 | 0 | 0 | 219.7 | 231.9
2026-08-17 | 22:00:00 | 1.1 | 2 | 226.3 | 236.83 | 1.85 | 13.12 | 225.3 | 234.9 | 0.29 | 0.54 | 223 | 235 | 0 | 0 | 226 | 234.2
2026-08-17 | 23:00:00 | 1.3 | 3.2 | 231.67 | 241.2 | 1.41 | 13.11 | 232.4 | 241.1 | 0.28 | 0.3 | 232.7 | 241.2 | 0 | 0 | 231.7 | 239
2026-08-18 | 00:00:00 | 1 | 2.3 | 231.27 | 241.8 | 1.4 | 5.8 | 230.8 | 241.5 | 0.28 | 0.77 | 232 | 241.4 | 0 | 0 | 232.3 | 239
2026-08-18 | 01:00:00 | 1.1 | 2 | 232.16 | 243.09 | 1.47 | 2.06 | 233.1 | 242.6 | 0.53 | 0.58 | 234.3 | 242.7 | 0 | 0 | 233.2 | 240.1
2026-08-18 | 02:00:00 | 1 | 2.5 | 238.22 | 243.29 | 1.47 | 1.87 | 237.3 | 242.9 | 0.53 | 0.54 | 237.1 | 243 | 0 | 0 | 235 | 241.7
2026-08-18 | 03:00:00 | 0.9 | 3.1 | 234.35 | 244.48 | 1.45 | 1.87 | 235.1 | 243.6 | 0.52 | 0.53 | 235 | 243.7 | 0 | 0 | 235 | 241.1
2026-08-18 | 04:00:00 | 1.2 | 1.9 | 231.67 | 242.29 | 1.4 | 3.49 | 230.4 | 242 | 0.28 | 0.53 | 230.7 | 242.3 | 0 | 0 | 231.9 | 240.5
2026-08-18 | 05:00:00 | 0.9 | 12.2 | 224.32 | 249.64 | 1.45 | 18.64 | 224.5 | 247.4 | 0.32 | 6.69 | 225.1 | 248.2 | 0 | 0 | 224.2 | 249.2
2026-08-18 | 06:00:00 | 1.2 | 12.9 | 214.89 | 243.48 | 1.46 | 13.17 | 212.6 | 243.1 | 0.35 | 0.94 | 213.4 | 242.9 | 0 | 0 | 213.2 | 242.6
2026-08-18 | 07:00:00 | 1.5 | 13 | 216.97 | 241.89 | 1.89 | 13.81 | 219.7 | 241.1 | 0.54 | 0.74 | 219.5 | 241.6 | 0 | 0 | 215.6 | 238.4
2026-08-18 | 08:00:00 | 1.3 | 13.2 | 218.86 | 248.35 | 1.81 | 13.71 | 223.5 | 247.4 | 0.3 | 0.57 | 221.9 | 244.8 | 0 | 0 | 223.7 | 244.4
2026-08-18 | 09:00:00 | 1.9 | 31.3 | 208.13 | 242.39 | 1.82 | 13.62 | 214.7 | 241.5 | 0.3 | 0.33 | 214.5 | 242 | 0 | 0 | 213.7 | 240.6
2026-08-18 | 10:00:00 | 1.3 | 13.1 | 223.13 | 244.18 | 1.71 | 13.43 | 223.6 | 243.7 | 0.3 | 6.6 | 224.6 | 243.6 | 0 | 0 | 224.7 | 241.7
2026-08-18 | 11:00:00 | 1.2 | 3.3 | 219.95 | 242.69 | 1.98 | 3.42 | 221.2 | 242.2 | 0.3 | 1.06 | 220.9 | 242.3 | 0 | 0 | 221.9 | 239.3
2026-08-18 | 12:00:00 | 1 | 4.1 | 228.79 | 243.98 | 1.92 | 2.64 | 225.3 | 243.1 | 0.54 | 1.11 | 225.4 | 243.3 | 0 | 0 | 227.1 | 242.9
2026-08-18 | 13:00:00 | 1.1 | 12.9 | 222.23 | 242.29 | 1.61 | 21.33 | 221.4 | 241.3 | 0.55 | 9.37 | 221.2 | 241.5 | 0 | 0 | 219.9 | 241.1
2026-08-18 | 14:00:00 | 1.1 | 3.9 | 221.24 | 242.69 | 1.85 | 10.89 | 217.2 | 241.8 | 0.53 | 9.36 | 218.1 | 241.2 | 0 | 0 | 216.1 | 241.1
2026-08-18 | 15:00:00 | 1.3 | 22.5 | 207.44 | 242.79 | 2.13 | 18.79 | 205.7 | 242 | 0.6 | 12.09 | 206.3 | 241.9 | 0 | 0 | 205.2 | 242
2026-08-18 | 16:00:00 | 1.4 | 22.9 | 206.35 | 236.14 | 2.29 | 20.6 | 206.8 | 235.3 | 1.05 | 1.19 | 207 | 235.4 | 0 | 0 | 208 | 236.1
2026-08-18 | 17:00:00 | 2 | 9.2 | 213.99 | 241.8 | 2.46 | 14.41 | 211.4 | 241.2 | 0.84 | 1.15 | 211.4 | 240.8 | 0 | 0 | 213.5 | 239.9
2026-08-18 | 18:00:00 | 1.8 | 19.1 | 216.77 | 240.8 | 2.37 | 6.28 | 221 | 239.7 | 0.82 | 1.73 | 221.8 | 240 | 0 | 0 | 218.7 | 239.9
2026-08-18 | 19:00:00 | 1.5 | 18.5 | 220.35 | 242.89 | 2.22 | 13.77 | 218.5 | 242.1 | 0.55 | 1.13 | 218.7 | 241.6 | 0 | 0 | 220.4 | 242.6
2026-08-18 | 20:00:00 | 1.9 | 4.7 | 228.39 | 240.9 | 2.24 | 4.25 | 227.7 | 241 | 0.61 | 1.2 | 228.3 | 240.9 | 0 | 0 | 228.4 | 239.3
2026-08-18 | 21:00:00 | 1.2 | 3.4 | 232.76 | 242.99 | 1.69 | 3.35 | 233.6 | 242 | 0.31 | 2.36 | 232.2 | 242 | 0 | 0 | 233 | 239.9
2026-08-18 | 22:00:00 | 1.2 | 3.8 | 234.05 | 240.6 | 1.58 | 2.42 | 233.9 | 240.3 | 0.54 | 0.59 | 233.9 | 241.8 | 0 | 0 | 233.3 | 239.9
2026-08-18 | 23:00:00 | 1.1 | 4.1 | 229.18 | 244.08 | 1.51 | 2 | 230.5 | 243.9 | 0.52 | 0.55 | 231.6 | 244.1 | 0 | 0 | 231.9 | 244.4
2026-08-19 | 00:00:00 | 1.1 | 3.8 | 233.26 | 244.28 | 1.35 | 6.08 | 235 | 244.3 | 0.29 | 0.54 | 236 | 244.2 | 0 | 0 | 238.4 | 244.4
2026-08-19 | 01:00:00 | 1 | 2 | 235.34 | 241.4 | 1.35 | 1.68 | 235.1 | 240.5 | 0.28 | 0.3 | 235.7 | 241.5 | 0 | 0 | 237.6 | 239.8
2026-08-19 | 02:00:00 | 1 | 1.9 | 236.23 | 240.9 | 1.4 | 6.73 | 236.7 | 241 | 0.29 | 1.62 | 236.9 | 240.6 | 0 | 0 | 239 | 239.8
2026-08-19 | 03:00:00 | 1 | 3.7 | 235.54 | 241.2 | 1.56 | 1.87 | 236.1 | 240.8 | 0.54 | 0.57 | 236.3 | 240.6 | 0 | 0 | 237.3 | 239.3
2026-08-19 | 04:00:00 | 1 | 4.2 | 231.47 | 250.73 | 1.5 | 12.97 | 230.5 | 250.2 | 0.53 | 12.29 | 231.4 | 249.9 | 0 | 0 | 231.7 | 247.2
2026-08-19 | 05:00:00 | 1.1 | 3.6 | 224.82 | 248.15 | 1.59 | 3.17 | 222.1 | 247.2 | 0.59 | 1.45 | 222.3 | 247.3 | 0 | 0 | 221.7 | 244.4
2026-08-19 | 06:00:00 | 0.9 | 12.7 | 218.86 | 241.89 | 1.64 | 12.84 | 212.5 | 242 | 0.3 | 4.35 | 212.6 | 241.9 | 0 | 0 | 216.1 | 239.9
2026-08-19 | 07:00:00 | 1.2 | 16.7 | 219.35 | 243.68 | 1.48 | 13.49 | 221.5 | 243.5 | 0.3 | 0.34 | 219.8 | 243.8 | 0 | 0 | 219.2 | 244
2026-08-19 | 08:00:00 | 1.2 | 12.3 | 219.85 | 243.19 | 1.67 | 9.08 | 217.9 | 242.6 | 0.3 | 0.83 | 218.3 | 242.8 | 0 | 0 | 220.2 | 240.5
2026-08-19 | 09:00:00 | 1 | 12.6 | 217.86 | 247.65 | 2.02 | 3.06 | 215.5 | 246.4 | 0.52 | 0.61 | 215.9 | 246.2 | 0 | 0 | 216.1 | 245.8
2026-08-19 | 10:00:00 | 0.9 | 13.3 | 226.6 | 249.44 | 2.21 | 8.44 | 228.7 | 248.8 | 0.52 | 6.97 | 228.7 | 248.2 | 0 | 0 | 230 | 246
2026-08-19 | 11:00:00 | 1 | 4 | 229.48 | 245.87 | 1.68 | 13.52 | 229.4 | 245.2 | 0.3 | 0.56 | 230.3 | 244.9 | 0 | 0 | 229.6 | 242.9
2026-08-19 | 12:00:00 | 1.2 | 20.6 | 221.74 | 244.58 | 1.75 | 14.22 | 221.4 | 243.5 | 0.3 | 0.58 | 221.8 | 243.3 | 0 | 0 | 223 | 242.9
2026-08-19 | 13:00:00 | 1.5 | 23 | 219.55 | 241.4 | 1.77 | 9.15 | 222.4 | 241.1 | 0.31 | 1.11 | 222.9 | 241.9 | 0 | 0 | 223.7 | 241.1
2026-08-19 | 14:00:00 | 1.1 | 14.1 | 222.03 | 242.19 | 1.53 | 2.1 | 222.7 | 241.5 | 0.55 | 0.61 | 223 | 240.9 | 0 | 0 | 222.8 | 241.7
2026-08-19 | 15:00:00 | 1.3 | 22.4 | 201.88 | 243.68 | 1.53 | 13.02 | 201.4 | 242.2 | 0.54 | 0.81 | 201.6 | 242.6 | 0 | 0 | 205.7 | 242.7
2026-08-19 | 16:00:00 | 1.8 | 19.8 | 196.61 | 235.84 | 2.45 | 33.48 | 194.8 | 233.9 | 0.54 | 11.34 | 196.7 | 232.8 | 0 | 0 | 195.7 | 234.2
2026-08-19 | 17:00:00 | 7.6 | 25.3 | 201.68 | 232.66 | 2.49 | 14.18 | 202.6 | 231.6 | 0.86 | 1.18 | 204.7 | 231.8 | 0 | 0 | 205.2 | 227.4
2026-08-19 | 18:00:00 | 1.9 | 18.9 | 201.68 | 236.93 | 2.12 | 3.47 | 201.8 | 235.2 | 0.85 | 1.14 | 202.9 | 234.4 | 0 | 0 | 201.2 | 234.2
2026-08-19 | 19:00:00 | 1.5 | 13.1 | 220.64 | 241.6 | 2.19 | 14.47 | 221.4 | 240.7 | 0.79 | 1.29 | 222.1 | 240.4 | 0 | 0 | 218.7 | 241.1
2026-08-19 | 20:00:00 | 1.9 | 2.9 | 222.73 | 239.21 | 2.41 | 7.87 | 221.9 | 238.1 | 0.86 | 1.49 | 222.3 | 238.1 | 0 | 0 | 220.9 | 238.4
2026-08-19 | 21:00:00 | 1.4 | 3.9 | 230.87 | 239.71 | 1.77 | 3.61 | 232.6 | 240 | 0.29 | 0.89 | 232.9 | 239.9 | 0 | 0 | 232.5 | 239.3
2026-08-19 | 22:00:00 | 1.1 | 3.8 | 234.45 | 242.59 | 1.58 | 3.49 | 234.4 | 242.4 | 0.29 | 0.3 | 235.5 | 242.7 | 0 | 0 | 233.9 | 239.3
2026-08-19 | 23:00:00 | 1.1 | 1.9 | 234.35 | 241.6 | 1.75 | 2.56 | 235.7 | 240.9 | 0.28 | 0.65 | 236 | 241.9 | 0 | 0 | 235.6 | 241.4
2026-08-20 | 00:00:00 | 1.1 | 3.7 | 232.76 | 242.59 | 1.5 | 2.25 | 235.7 | 241.5 | 0.55 | 0.58 | 234.5 | 241.8 | 0 | 0 | 233.9 | 240.5
2026-08-20 | 01:00:00 | 1 | 4 | 239.51 | 243.58 | 1.5 | 4.31 | 239.5 | 243 | 0.53 | 0.56 | 241.1 | 243.1 | 0 | 0 | 240.5 | 242
2026-08-20 | 02:00:00 | 0.8 | 3.8 | 239.11 | 244.58 | 1.49 | 4.74 | 238.7 | 243.7 | 0.52 | 0.55 | 239 | 243.8 | 0 | 0 | 240.6 | 242
2026-08-20 | 03:00:00 | 0.9 | 12.6 | 228.99 | 241.99 | 1.48 | 2.26 | 234.1 | 241.4 | 0.29 | 0.55 | 234.4 | 241.5 | 0 | 0 | 235.6 | 241.1
2026-08-20 | 04:00:00 | 0.9 | 4.1 | 229.88 | 242.89 | 1.39 | 1.74 | 229.6 | 242.8 | 0.28 | 0.35 | 229.5 | 243.1 | 0 | 0 | 231.9 | 240.8
2026-08-20 | 05:00:00 | 0.9 | 13 | 227.6 | 249.24 | 1.49 | 13.29 | 223.3 | 249.1 | 0.3 | 11.96 | 223.3 | 249.5 | 0 | 0 | 223.7 | 245.3
2026-08-20 | 06:00:00 | 0.9 | 13.1 | 226.8 | 242.89 | 1.57 | 17.83 | 226.8 | 242.3 | 0.35 | 6.98 | 228 | 242.6 | 0 | 0 | 226.6 | 239.9
2026-08-20 | 07:00:00 | 1.2 | 13 | 216.87 | 246.56 | 1.59 | 7.63 | 225.7 | 245 | 0.54 | 4.76 | 226.9 | 245.1 | 0 | 0 | 219.9 | 245.6
2026-08-20 | 08:00:00 | 0.9 | 12.8 | 222.43 | 244.97 | 1.58 | 13.4 | 221 | 244.5 | 0.52 | 1.1 | 220.6 | 244.6 | 0 | 0 | 221.4 | 244.4
2026-08-20 | 09:00:00 | 1 | 13.7 | 222.23 | 245.77 | 1.82 | 11.69 | 223.3 | 244.6 | 0.52 | 10.09 | 223.1 | 244.5 | 0 | 0 | 222.6 | 244.8
2026-08-20 | 10:00:00 | 1 | 7.6 | 224.62 | 248.25 | 1.88 | 6.01 | 222.8 | 247 | 0.51 | 0.76 | 223 | 247.8 | 0 | 0 | 220.7 | 247.8
2026-08-20 | 11:00:00 | 1 | 13.1 | 218.76 | 242.79 | 1.88 | 13.69 | 219.5 | 242.2 | 0.3 | 6.92 | 222.2 | 241.3 | 0 | 0 | 218.5 | 242.3
2026-08-20 | 12:00:00 | 0.9 | 13.7 | 217.57 | 245.67 | 1.75 | 7.11 | 218.8 | 244.3 | 0.4 | 0.8 | 219.7 | 244.4 | 0 | 0 | 218.5 | 240.5
2026-08-20 | 13:00:00 | 1.5 | 20.7 | 205.25 | 242.19 | 1.77 | 3.09 | 214.4 | 240.6 | 0.3 | 0.78 | 214.5 | 241.1 | 0 | 0 | 215.3 | 241.1
2026-08-20 | 14:00:00 | 1.5 | 13.1 | 221.14 | 243.58 | 1.87 | 13.16 | 227.1 | 243.2 | 0.31 | 1.09 | 227.4 | 243.1 | 0 | 0 | 227.6 | 242
2026-08-20 | 15:00:00 | 1.4 | 12.5 | 220.55 | 244.58 | 1.77 | 16.7 | 215.5 | 242.8 | 0.54 | 9.69 | 215.4 | 243.6 | 0 | 0 | 218.7 | 244.6
2026-08-20 | 16:00:00 | 1.8 | 23.7 | 204.06 | 237.33 | 2.59 | 23.34 | 200 | 234.7 | 0.86 | 1.32 | 203 | 234.9 | 0 | 0 | 199.3 | 235.3
2026-08-20 | 17:00:00 | 1.8 | 12.8 | 211.11 | 242.99 | 2.25 | 20.87 | 208.9 | 240.6 | 0.84 | 1.16 | 208.5 | 240.8 | 0 | 0 | 208.5 | 238.2
2026-08-20 | 18:00:00 | 1.9 | 21.4 | 219.85 | 239.31 | 2.18 | 3.11 | 220 | 236.6 | 0.79 | 0.96 | 219.3 | 236.5 | 0 | 0 | 218.2 | 239
2026-08-20 | 19:00:00 | 1.6 | 14.4 | 217.57 | 240.21 | 2 | 14.42 | 216.7 | 239.9 | 0.78 | 1.18 | 217.1 | 239.7 | 0 | 0 | 216.7 | 237.8
2026-08-20 | 20:00:00 | 1.8 | 14.4 | 217.37 | 240.8 | 2.33 | 21.05 | 216.1 | 239.1 | 0.38 | 1.18 | 216.4 | 239.2 | 0 | 0 | 216.7 | 239.9
2026-08-20 | 21:00:00 | 1.8 | 4.5 | 226.11 | 238.72 | 1.61 | 12.59 | 227.5 | 239.1 | 0.28 | 0.55 | 227.6 | 238.6 | 0 | 0 | 228.2 | 238.2
2026-08-20 | 22:00:00 | 1.1 | 1.9 | 236.23 | 243.38 | 1.43 | 1.72 | 236.5 | 242.3 | 0.28 | 0.3 | 236.7 | 242.6 | 0 | 0 | 237.6 | 243.5
2026-08-20 | 23:00:00 | 0.9 | 2 | 236.33 | 241.5 | 1.49 | 2.06 | 236.8 | 240.7 | 0.29 | 0.72 | 236.4 | 240.8 | 0 | 0 | 238.2 | 238.7
2026-08-21 | 00:00:00 | 0.9 | 2.2 | 237.43 | 242.49 | 1.5 | 1.87 | 236.9 | 241.9 | 0.53 | 0.57 | 238.1 | 241.9 | 0 | 0 | 236.1 | 241.4
2026-08-21 | 01:00:00 | 0.9 | 3.3 | 234.75 | 242.69 | 1.51 | 12.97 | 232.1 | 242.7 | 0.52 | 0.55 | 232.4 | 242.6 | 0 | 0 | 231.9 | 241.1
2026-08-21 | 02:00:00 | 0.8 | 3.8 | 237.62 | 243.09 | 1.4 | 1.78 | 238.5 | 242.6 | 0.28 | 0.54 | 239.1 | 243.8 | 0 | 0 | 239.6 | 241.4
2026-08-21 | 03:00:00 | 0.8 | 1.6 | 237.72 | 242.59 | 1.39 | 1.71 | 237.8 | 241.5 | 0.28 | 0.3 | 238.1 | 242 | 0 | 0 | 239.3 | 240.5
2026-08-21 | 04:00:00 | 0.8 | 1.7 | 232.06 | 243.58 | 1.4 | 5.91 | 233.3 | 242.9 | 0.28 | 0.29 | 234.6 | 243.3 | 0 | 0 | 235 | 241.4
2026-08-21 | 05:00:00 | 0.9 | 12.5 | 221.64 | 248.85 | 1.45 | 12.3 | 221.3 | 244.5 | 0.28 | 11.59 | 221.2 | 248.6 | 0 | 0 | 221.7 | 248.1
2026-08-21 | 06:00:00 | 0.9 | 16.8 | 226.11 | 241.4 | 1.67 | 13.63 | 223.7 | 240.9 | 0.53 | 1.27 | 223.8 | 241 | 0 | 0 | 219.4 | 240.5
2026-08-21 | 07:00:00 | 0.9 | 19.8 | 217.27 | 245.77 | 1.76 | 14.68 | 220 | 244.8 | 0.52 | 10.31 | 219.3 | 245 | 0 | 0 | 219.2 | 243.5
2026-08-21 | 08:00:00 | 1 | 20.8 | 219.75 | 240.21 | 1.75 | 14.69 | 220.3 | 239.4 | 0.31 | 4.8 | 220.5 | 239.2 | 0 | 0 | 218.5 | 240.2
2026-08-21 | 09:00:00 | 1 | 12.1 | 227.6 | 244.38 | 1.75 | 10.36 | 225.4 | 242.2 | 0.31 | 9.23 | 225.6 | 242.3 | 0 | 0 | 225.5 | 241.5
2026-08-21 | 10:00:00 | 1.2 | 13.4 | 226.01 | 243.98 | 1.69 | 7.7 | 224.8 | 243.3 | 0.32 | 6.57 | 226.1 | 243.8 | 0 | 0 | 226.4 | 242.5
2026-08-21 | 11:00:00 | 1.2 | 15.5 | 224.72 | 241.5 | 1.72 | 13.09 | 224.5 | 241.1 | 0.58 | 1.19 | 228.9 | 239.6 | 0 | 0 | 224 | 239.3
2026-08-21 | 12:00:00 | 1.3 | 12.4 | 222.83 | 242.39 | 2.37 | 3.43 | 226.3 | 241.2 | 1.05 | 1.18 | 228.2 | 242.6 | 0 | 0 | 226.1 | 240.3
2026-08-21 | 13:00:00 | 1.4 | 4.2 | 224.72 | 242.79 | 1.51 | 2.79 | 226.3 | 242.4 | 0.53 | 1.12 | 226.4 | 242.6 | 0 | 0 | 229.6 | 242.3
2026-08-21 | 14:00:00 | 1.1 | 12.8 | 220.25 | 243.38 | 1.51 | 9.99 | 216.9 | 242.6 | 0.54 | 9.42 | 216.8 | 242.8 | 0 | 0 | 218.7 | 240.5
2026-08-21 | 15:00:00 | 1.3 | 12 | 215.08 | 235.44 | 1.82 | 8.56 | 211.6 | 232.4 | 0.8 | 1.1 | 212.2 | 233 | 0 | 0 | 214.6 | 232.2
2026-08-21 | 16:00:00 | 1.5 | 17.5 | 195.42 | 233.95 | 2.13 | 20.02 | 197 | 231.1 | 0.78 | 11.77 | 197.5 | 231.8 | 0 | 0 | 199.3 | 231.7
2026-08-21 | 17:00:00 | 1.3 | 13.3 | 198.2 | 242.99 | 2.26 | 14.54 | 199.5 | 242.6 | 0.6 | 1.4 | 198.8 | 242.7 | 0 | 0 | 200.3 | 243.1
2026-08-21 | 18:00:00 | 2 | 8.9 | 222.63 | 242.39 | 2.41 | 4.71 | 225 | 241.8 | 0.87 | 1.11 | 225.1 | 241.8 | 0 | 0 | 224.8 | 243.1
2026-08-21 | 19:00:00 | 1.7 | 14.7 | 221.24 | 240.01 | 2.21 | 14.59 | 221.4 | 241.3 | 0.86 | 1.36 | 221.3 | 239.4 | 0 | 0 | 222.2 | 238.2
2026-08-21 | 20:00:00 | 1.8 | 13.8 | 223.33 | 241.5 | 2.42 | 3.62 | 226.4 | 241 | 0.54 | 1.4 | 226.3 | 241.6 | 0 | 0 | 226.1 | 240.2
2026-08-21 | 21:00:00 | 1.3 | 3.2 | 227.2 | 242.69 | 1.72 | 2.63 | 224.5 | 241.8 | 0.28 | 0.69 | 224.3 | 242.1 | 0 | 0 | 224.3 | 240.8
2026-08-21 | 22:00:00 | 1.1 | 4 | 233.45 | 240.7 | 1.34 | 2.01 | 233.9 | 240.3 | 0.28 | 0.3 | 234.9 | 240.4 | 0 | 0 | 235 | 241.4
2026-08-21 | 23:00:00 | 1.2 | 1.7 | 231.17 | 242.89 | 1.44 | 1.87 | 234 | 242.2 | 0.29 | 5.6 | 234.2 | 243.2 | 0 | 0 | 235.5 | 243.5
2026-08-22 | 00:00:00 | 0.9 | 3.1 | 230.97 | 242.19 | 1.42 | 5.12 | 233.1 | 242.3 | 0.28 | 0.56 | 232.2 | 242 | 0 | 0 | 233.9 | 241.4
2026-08-22 | 01:00:00 | 1 | 2.2 | 238.02 | 242.19 | 1.27 | 1.72 | 237.6 | 242.3 | 0.28 | 0.31 | 238.2 | 242.3 | 0 | 0 | 239.2 | 241.4
2026-08-22 | 02:00:00 | 0.8 | 3.4 | 238.22 | 242.89 | 1.32 | 1.97 | 238.1 | 242.3 | 0.29 | 0.69 | 238.4 | 242.7 | 0 | 0 | 235 | 241.4
2026-08-22 | 03:00:00 | 0.9 | 3.8 | 239.71 | 244.68 | 1.42 | 1.8 | 239.3 | 243.8 | 0.54 | 0.57 | 240.1 | 243.9 | 0 | 0 | 238.2 | 243.5
2026-08-22 | 04:00:00 | 0.9 | 3.7 | 236.73 | 244.08 | 1.31 | 1.82 | 236.3 | 243.9 | 0.28 | 0.55 | 236.8 | 244.2 | 0 | 0 | 237.9 | 243.5
2026-08-22 | 05:00:00 | 0.8 | 12 | 215.48 | 243.48 | 1.39 | 12.12 | 218.1 | 243.4 | 0.29 | 11.6 | 218.5 | 243.7 | 0 | 0 | 216.8 | 243.2
2026-08-22 | 06:00:00 | 0.9 | 12.4 | 219.35 | 242.29 | 1.54 | 12.84 | 214.5 | 241.7 | 0.29 | 6.84 | 215.1 | 242.4 | 0 | 0 | 216.8 | 242
2026-08-22 | 07:00:00 | 0.9 | 12.4 | 216.18 | 239.11 | 1.94 | 13.31 | 213.8 | 237.9 | 0.58 | 6.06 | 214.3 | 237.7 | 0 | 0 | 216.7 | 239.4
2026-08-22 | 08:00:00 | 0.9 | 12.1 | 210.42 | 244.58 | 1.9 | 19.58 | 212.9 | 243.7 | 0.7 | 0.76 | 214.4 | 244.1 | 0 | 0 | 212.2 | 242.2
2026-08-22 | 09:00:00 | 0.9 | 19 | 208.93 | 240.01 | 2.19 | 13.68 | 211.8 | 238.9 | 0.7 | 0.79 | 212.4 | 239.2 | 0 | 0 | 214.4 | 237.9
2026-08-22 | 10:00:00 | 1 | 13.7 | 215.88 | 243.88 | 2 | 14.26 | 217.3 | 243.2 | 0.69 | 0.73 | 219.8 | 242.8 | 0 | 0 | 218.7 | 244.4
2026-08-22 | 11:00:00 | 1.1 | 21.5 | 215.68 | 241.7 | 1.96 | 13.73 | 217 | 240.4 | 0.56 | 6.97 | 217.7 | 240.8 | 0 | 0 | 216.1 | 239.6
2026-08-22 | 12:00:00 | 2.1 | 15.9 | 214.39 | 241.2 | 1.53 | 2.65 | 218.1 | 240.6 | 0.55 | 1.1 | 217.2 | 240.7 | 0 | 0 | 217.3 | 240.6
2026-08-22 | 13:00:00 | 1.4 | 23.1 | 214.29 | 241.4 | 1.51 | 12.28 | 216.3 | 241.4 | 0.54 | 1.17 | 216.8 | 240.8 | 0 | 0 | 216.5 | 241.7
2026-08-22 | 14:00:00 | 2.6 | 28.4 | 207.34 | 233.16 | 1.7 | 2.65 | 213.8 | 231.4 | 0.67 | 1.62 | 215.1 | 231.1 | 0 | 0 | 213.9 | 232.2
2026-08-22 | 15:00:00 | 2.1 | 9.1 | 215.88 | 236.93 | 1.85 | 11.97 | 215.1 | 236.4 | 1.09 | 1.66 | 217 | 236.5 | 0 | 0 | 218.2 | 235.7
2026-08-22 | 16:00:00 | 1.6 | 23.1 | 214.89 | 240.6 | 1.98 | 13.1 | 214 | 240.1 | 1.06 | 1.14 | 214.3 | 235.9 | 0 | 0 | 217.5 | 239.9
2026-08-22 | 17:00:00 | 1.9 | 19.3 | 213.99 | 239.21 | 2.17 | 13.66 | 216.1 | 238.4 | 0.56 | 1.12 | 216.3 | 238.7 | 0 | 0 | 216.8 | 237.9
2026-08-22 | 18:00:00 | 1.5 | 13.1 | 224.02 | 241.5 | 2.11 | 3.27 | 223.3 | 240.8 | 0.54 | 0.58 | 223.9 | 241.2 | 0 | 0 | 227.6 | 239.8
2026-08-22 | 19:00:00 | 1.7 | 30.2 | 205.95 | 238.72 | 2.04 | 14.61 | 213.3 | 238.3 | 0.53 | 1.38 | 210.7 | 237.8 | 0 | 0 | 213.9 | 234.7
2026-08-22 | 20:00:00 | 1.7 | 9.9 | 228.19 | 240.7 | 2.58 | 3.47 | 230.4 | 240.6 | 0.68 | 1.56 | 231 | 239.8 | 0 | 0 | 230.8 | 238.7
2026-08-22 | 21:00:00 | 1.2 | 4.3 | 228.19 | 249.04 | 2.36 | 3.19 | 228.4 | 248.2 | 0.54 | 0.76 | 228.4 | 248.1 | 0 | 0 | 228.4 | 245
2026-08-22 | 22:00:00 | 1 | 2.6 | 233.55 | 242.59 | 1.45 | 3.92 | 235 | 242.3 | 0.53 | 0.55 | 235.5 | 242 | 0 | 0 | 238.7 | 239
2026-08-22 | 23:00:00 | 1 | 2.6 | 231.77 | 244.28 | 1.44 | 2.05 | 233.5 | 244 | 0.53 | 0.55 | 233.8 | 242.2 | 0 | 0 | 233.9 | 239.5
2026-08-23 | 00:00:00 | 0.9 | 3.5 | 238.82 | 243.09 | 1.32 | 7 | 239 | 242.3 | 0.28 | 0.54 | 239.7 | 242.6 | 0 | 0 | 238.7 | 240.3
2026-08-23 | 01:00:00 | 0.9 | 3.8 | 239.51 | 242.49 | 1.29 | 5.66 | 239.3 | 242.3 | 0.28 | 0.32 | 239.7 | 242.6 | 0 | 0 | 239.6 | 241.3
2026-08-23 | 02:00:00 | 0.8 | 2.7 | 239.11 | 244.97 | 1.29 | 1.66 | 238.6 | 245.2 | 0.28 | 0.3 | 239 | 244.9 | 0 | 0 | 239.5 | 245.3
2026-08-23 | 03:00:00 | 0.8 | 3.6 | 238.62 | 243.29 | 1.43 | 3.89 | 238.5 | 242.7 | 0.28 | 0.68 | 237.7 | 242.9 | 0 | 0 | 239.5 | 240.8
2026-08-23 | 04:00:00 | 0.8 | 3.2 | 232.06 | 243.09 | 1.45 | 1.83 | 231.5 | 242.6 | 0.28 | 0.56 | 232.2 | 242.3 | 0 | 0 | 226.8 | 240.8
2026-08-23 | 05:00:00 | 0.9 | 12.5 | 224.91 | 242.99 | 1.29 | 12.54 | 222 | 242.5 | 0.28 | 11.86 | 223.2 | 243 | 0 | 0 | 221.7 | 241.3
2026-08-23 | 06:00:00 | 0.8 | 12.7 | 223.82 | 242.39 | 1.4 | 13.55 | 223.1 | 241.9 | 0.3 | 0.94 | 223.9 | 243 | 0 | 0 | 224.3 | 241.7
2026-08-23 | 07:00:00 | 0.8 | 16.2 | 218.46 | 240.5 | 1.69 | 19.06 | 213.2 | 240 | 0.31 | 6.42 | 215.3 | 238.8 | 0 | 0 | 212.5 | 238.4
2026-08-23 | 08:00:00 | 0.9 | 14.6 | 208.23 | 247.95 | 1.83 | 10.77 | 205.3 | 246.5 | 0.3 | 9.29 | 208.1 | 246.4 | 0 | 0 | 208.1 | 243.5
2026-08-23 | 09:00:00 | 1 | 12.5 | 215.28 | 241.8 | 1.52 | 19.97 | 215.1 | 241.6 | 0.3 | 1.81 | 215.6 | 241 | 0 | 0 | 213.5 | 242.3
2026-08-23 | 10:00:00 | 1.7 | 21.4 | 207.34 | 240.01 | 1.32 | 12.46 | 212.9 | 238.8 | 0.3 | 6.96 | 210.6 | 240.3 | 0 | 0 | 210.5 | 237.9
2026-08-23 | 11:00:00 | 1.6 | 14.4 | 216.28 | 244.08 | 1.54 | 7.79 | 219.7 | 243.8 | 0.58 | 6.9 | 219.7 | 243.9 | 0 | 0 | 220.2 | 241.7
2026-08-23 | 12:00:00 | 1.7 | 22.4 | 219.35 | 245.67 | 1.7 | 11.21 | 219.8 | 245.9 | 0.55 | 10.01 | 220.7 | 244.7 | 0 | 0 | 218.7 | 244.7
2026-08-23 | 13:00:00 | 1.6 | 5.3 | 219.45 | 243.19 | 2.21 | 21.61 | 215.6 | 242.4 | 1.03 | 9.83 | 214.2 | 243.1 | 0 | 0 | 217.5 | 242.9
2026-08-23 | 14:00:00 | 2 | 3 | 216.18 | 241.6 | 1.87 | 11.55 | 210.1 | 240 | 0.56 | 9.84 | 212.3 | 240.2 | 0 | 0 | 212.1 | 241.1
2026-08-23 | 15:00:00 | 1.5 | 8.9 | 216.97 | 237.33 | 1.79 | 17.11 | 214.8 | 235.5 | 0.54 | 11.67 | 214.6 | 235.4 | 0 | 0 | 213.3 | 235.6
2026-08-23 | 16:00:00 | 1.3 | 20.3 | 212.01 | 239.11 | 1.79 | 12.99 | 208.5 | 237.1 | 0.54 | 1.15 | 208.6 | 236.8 | 0 | 0 | 209.3 | 237.6
2026-08-23 | 17:00:00 | 1.8 | 19.5 | 207.83 | 235.04 | 2.43 | 20.3 | 203.4 | 235.1 | 1.04 | 1.17 | 204.1 | 235 | 0 | 0 | 206.5 | 237
2026-08-23 | 18:00:00 | 2.1 | 19.1 | 211.91 | 238.52 | 2.51 | 3.55 | 217.8 | 237.3 | 0.8 | 1.07 | 219.7 | 237.7 | 0 | 0 | 216.7 | 237.6
2026-08-23 | 19:00:00 | 1.4 | 18.2 | 219.95 | 240.31 | 2.25 | 14.25 | 223.7 | 240.1 | 0.78 | 1.05 | 223 | 238.7 | 0 | 0 | 222.2 | 237.3
2026-08-23 | 20:00:00 | 2 | 4.8 | 231.17 | 239.81 | 2.11 | 3.3 | 231.5 | 239.6 | 0.41 | 1.33 | 231.6 | 239.5 | 0 | 0 | 234.2 | 238.7
2026-08-23 | 21:00:00 | 1.8 | 4.2 | 233.16 | 241.8 | 1.64 | 2.28 | 234 | 241.3 | 0.29 | 0.47 | 235 | 241.8 | 0 | 0 | 231.4 | 238.7
2026-08-23 | 22:00:00 | 1.2 | 3.2 | 228.19 | 241.8 | 1.32 | 1.76 | 231.4 | 242 | 0.28 | 0.3 | 232 | 242.2 | 0 | 0 | 230.1 | 241.4
2026-08-23 | 23:00:00 | 1 | 2.8 | 230.97 | 240.6 | 1.35 | 1.83 | 233 | 240.4 | 0.28 | 0.7 | 233.3 | 240.5 | 0 | 0 | 234 | 239.3
2026-08-24 | 00:00:00 | 0.9 | 3.6 | 234.05 | 241.7 | 1.45 | 1.8 | 233.8 | 241.3 | 0.53 | 0.57 | 233.9 | 241.4 | 0 | 0 | 236.4 | 239.3
2026-08-24 | 01:00:00 | 0.9 | 2.6 | 235.44 | 239.71 | 1.41 | 2.58 | 234.3 | 239.4 | 0.52 | 0.56 | 236 | 239.9 | 0 | 0 | 236.4 | 237.6
2026-08-24 | 02:00:00 | 0.8 | 3.4 | 233.85 | 241.5 | 1.42 | 1.84 | 235 | 241.2 | 0.52 | 0.54 | 234.2 | 241.3 | 0 | 0 | 233.9 | 240.2
2026-08-24 | 03:00:00 | 0.8 | 2.9 | 238.72 | 244.58 | 1.3 | 1.68 | 240.3 | 244.3 | 0.28 | 0.53 | 239.4 | 244.4 | 0 | 0 | 239.3 | 242.3
2026-08-24 | 04:00:00 | 0.9 | 12.7 | 231.27 | 244.08 | 1.33 | 1.68 | 229.7 | 243.5 | 0.28 | 0.3 | 230.1 | 244.2 | 0 | 0 | 229 | 242.6
2026-08-24 | 05:00:00 | 0.9 | 12.5 | 222.13 | 247.55 | 1.33 | 12.34 | 222.7 | 247.2 | 0.29 | 11.58 | 225.1 | 247.4 | 0 | 0 | 222.4 | 245.9
2026-08-24 | 06:00:00 | 0.9 | 12.4 | 213.99 | 243.09 | 1.39 | 12.7 | 208.3 | 240.8 | 0.35 | 0.92 | 209 | 241.2 | 0 | 0 | 210.7 | 239.9
2026-08-24 | 07:00:00 | 0.8 | 17.9 | 224.91 | 247.46 | 1.55 | 8 | 224.7 | 246.4 | 0.54 | 4.73 | 224.7 | 246.7 | 0 | 0 | 226 | 246.6
2026-08-24 | 08:00:00 | 0.8 | 14.3 | 215.08 | 252.22 | 1.39 | 13.7 | 213.8 | 250.9 | 0.3 | 1.11 | 215.8 | 251.2 | 0 | 0 | 216.5 | 249.1
2026-08-24 | 09:00:00 | 0.9 | 11.9 | 212.4 | 247.85 | 1.36 | 8.43 | 211.9 | 244.8 | 0.3 | 0.32 | 213.8 | 245.2 | 0 | 0 | 214.2 | 247.8
2026-08-24 | 10:00:00 | 0.9 | 12.5 | 220.35 | 239.11 | 1.35 | 24.78 | 216.5 | 237.1 | 0.3 | 6.71 | 218.6 | 237.1 | 0 | 0 | 216.8 | 236.1
2026-08-24 | 11:00:00 | 0.8 | 1.9 | 221.84 | 240.01 | 1.87 | 2.89 | 217.5 | 236.4 | 0.56 | 1.08 | 217.9 | 236.4 | 0 | 0 | 218.7 | 234.7
2026-08-24 | 12:00:00 | 1 | 12.4 | 214.39 | 241.8 | 2.46 | 14.62 | 213.4 | 241.2 | 1.05 | 1.14 | 213.8 | 241.5 | 0 | 0 | 215.8 | 241.7
2026-08-24 | 13:00:00 | 1 | 23.2 | 221.94 | 245.67 | 1.82 | 13.46 | 224.6 | 244.7 | 0.53 | 1.07 | 226.8 | 244.2 | 0 | 0 | 225.3 | 244.4
2026-08-24 | 14:00:00 | 1 | 2 | 230.77 | 244.77 | 1.94 | 5.16 | 228.4 | 243.5 | 0.53 | 1.06 | 230.8 | 244.1 | 0 | 0 | 230.1 | 244.7
2026-08-24 | 15:00:00 | 1.1 | 14 | 220.15 | 244.38 | 2.14 | 6.99 | 223.8 | 243.5 | 0.85 | 5.21 | 222.1 | 244.1 | 0 | 0 | 220.2 | 244.7
2026-08-24 | 16:00:00 | 1.6 | 23.2 | 195.62 | 239.41 | 2.14 | 26.42 | 196.6 | 238.4 | 0.85 | 1.42 | 195.5 | 238.1 | 0 | 0 | 194.7 | 237.9
2026-08-24 | 17:00:00 | 2.5 | 24.5 | 209.52 | 238.92 | 2.67 | 14.22 | 209.8 | 237.3 | 0.85 | 1.06 | 209.9 | 238.4 | 0 | 0 | 214.9 | 237.6
2026-08-24 | 18:00:00 | 2.4 | 25.9 | 211.51 | 238.32 | 2.33 | 6.54 | 219.4 | 238.3 | 0.8 | 0.98 | 219.7 | 238.5 | 0 | 0 | 221.9 | 239
2026-08-24 | 19:00:00 | 1.8 | 19.9 | 216.47 | 239.81 | 2.45 | 3.75 | 219.9 | 238.7 | 0.81 | 1.16 | 220.1 | 238.2 | 0 | 0 | 221.6 | 237.3
2026-08-24 | 20:00:00 | 1.9 | 5.2 | 228.19 | 241.3 | 2.5 | 14.41 | 225.9 | 240.6 | 0.4 | 1.11 | 226.4 | 241 | 0 | 0 | 226.1 | 237.9
2026-08-24 | 21:00:00 | 1.2 | 3.6 | 233.55 | 244.18 | 1.71 | 3.56 | 233.1 | 243 | 0.29 | 0.46 | 233.1 | 243.7 | 0 | 0 | 232.5 | 243.2
2026-08-24 | 22:00:00 | 1 | 2 | 234.25 | 245.07 | 1.6 | 2.11 | 232.7 | 243.8 | 0.28 | 1.78 | 231.6 | 243.6 | 0 | 0 | 236.4 | 241.7
2026-08-24 | 23:00:00 | 1 | 2.9 | 237.23 | 245.17 | 1.57 | 2.13 | 236.3 | 244.1 | 0.53 | 0.58 | 236.4 | 244.2 | 0 | 0 | 237.2 | 243.2
2026-08-25 | 00:00:00 | 0.9 | 3.3 | 234.05 | 242.19 | 1.43 | 13.27 | 231.2 | 241.9 | 0.53 | 0.55 | 232.9 | 241.8 | 0 | 0 | 231.9 | 242.6
2026-08-25 | 01:00:00 | 0.8 | 3.9 | 237.72 | 244.77 | 1.63 | 5.13 | 236.8 | 243.9 | 0.29 | 0.54 | 237.3 | 244.5 | 0 | 0 | 237.9 | 242
2026-08-25 | 02:00:00 | 0.8 | 3.9 | 240.7 | 244.97 | 1.34 | 1.65 | 240.4 | 243.8 | 0.29 | 0.3 | 240.4 | 244.3 | 0 | 0 | 242 | 242.6
2026-08-25 | 03:00:00 | 0.8 | 1.6 | 240.01 | 244.38 | 1.3 | 3.14 | 238.5 | 244.1 | 0.28 | 1.62 | 240.1 | 244.1 | 0 | 0 | 240.2 | 242
2026-08-25 | 04:00:00 | 0.8 | 3.8 | 231.27 | 244.08 | 1.48 | 4.18 | 226.3 | 243.2 | 0.55 | 0.57 | 229.2 | 243.4 | 0 | 0 | 229.8 | 242.6
2026-08-25 | 05:00:00 | 1.1 | 12.9 | 229.88 | 246.86 | 1.52 | 12.94 | 230.8 | 246.3 | 0.52 | 12.26 | 228.4 | 246.5 | 0 | 0 | 227.9 | 246.2
2026-08-25 | 06:00:00 | 0.9 | 12.7 | 223.03 | 242.49 | 1.47 | 6.41 | 224.1 | 241.5 | 0.53 | 1.44 | 223.3 | 241.1 | 0 | 0 | 225 | 239.9
2026-08-25 | 07:00:00 | 0.9 | 13.3 | 221.34 | 243.58 | 1.56 | 17.55 | 220.5 | 241.7 | 0.52 | 6.92 | 220.5 | 242.5 | 0 | 0 | 220.9 | 243.2
2026-08-25 | 08:00:00 | 1 | 20.5 | 217.07 | 241.5 | 1.66 | 12.95 | 217.5 | 240.4 | 0.29 | 0.78 | 216.2 | 240.7 | 0 | 0 | 213.2 | 241.4
2026-08-25 | 09:00:00 | 0.9 | 1.4 | 228.79 | 243.88 | 1.74 | 8.71 | 226.1 | 243.1 | 0.3 | 0.9 | 226.6 | 242.9 | 0 | 0 | 226.7 | 242.8
2026-08-25 | 10:00:00 | 0.9 | 12.8 | 212.01 | 241.7 | 1.63 | 17.74 | 204.3 | 241.1 | 0.3 | 6.46 | 205.5 | 240.3 | 0 | 0 | 210 | 237.5
2026-08-25 | 11:00:00 | 0.9 | 22.1 | 197.71 | 238.92 | 2.39 | 13.79 | 200.4 | 235.9 | 0.3 | 5.79 | 199.9 | 235.1 | 0 | 0 | 198.3 | 234.7
2026-08-25 | 12:00:00 | 1.4 | 25.1 | 215.68 | 235.44 | 2.6 | 3.65 | 214.5 | 234.4 | 1.04 | 1.14 | 214.9 | 234 | 0 | 0 | 214.4 | 234.7
2026-08-25 | 13:00:00 | 1.1 | 17.4 | 222.03 | 245.87 | 1.61 | 3.69 | 224.8 | 244.7 | 0.3 | 1.07 | 225 | 245.3 | 0 | 0 | 225.8 | 242.9
2026-08-25 | 14:00:00 | 1.1 | 12.6 | 221.14 | 245.67 | 1.69 | 13.17 | 221.4 | 244.4 | 0.29 | 0.75 | 222.2 | 244.5 | 0 | 0 | 220.6 | 241.7
2026-08-25 | 15:00:00 | 1.4 | 22 | 208.73 | 241.4 | 2.16 | 13.88 | 206.5 | 238.3 | 0.58 | 12.53 | 205.8 | 239.8 | 0 | 0 | 204 | 241.4
2026-08-25 | 16:00:00 | 6.4 | 33 | 202.97 | 237.03 | 2 | 30.86 | 196.4 | 237.5 | 0.59 | 1.29 | 200.4 | 237.7 | 0 | 0 | 198.9 | 238.4
2026-08-25 | 17:00:00 | 2 | 19.1 | 206.84 | 245.27 | 2.43 | 16.73 | 208.6 | 245.5 | 0.85 | 1.22 | 209.9 | 244.7 | 0 | 0 | 209.3 | 245.6
2026-08-25 | 18:00:00 | 1.5 | 18.4 | 223.43 | 242.89 | 2.17 | 8.98 | 225.4 | 241.4 | 0.81 | 1.13 | 226 | 242 | 0 | 0 | 226.8 | 239
2026-08-25 | 19:00:00 | 1.6 | 14.5 | 226.8 | 240.6 | 2.15 | 13.77 | 226.2 | 240 | 0.85 | 0.88 | 225.6 | 240.1 | 0 | 0 | 224.8 | 240.8
2026-08-25 | 20:00:00 | 1.9 | 3.1 | 224.91 | 238.42 | 2.32 | 3.51 | 223.7 | 237.7 | 0.6 | 1.27 | 223.6 | 237.9 | 0 | 0 | 221.4 | 235.3
2026-08-25 | 21:00:00 | 1.4 | 3.1 | 226.7 | 241.5 | 1.86 | 3.18 | 225.2 | 241.4 | 0.52 | 0.67 | 227.3 | 241.6 | 0 | 0 | 223.9 | 240.5
2026-08-25 | 22:00:00 | 1 | 2.6 | 235.44 | 242.29 | 1.37 | 2.21 | 234.6 | 241.9 | 0.29 | 0.53 | 234.9 | 242.1 | 0 | 0 | 234.8 | 240.9
2026-08-25 | 23:00:00 | 1.1 | 2.6 | 238.42 | 242.79 | 1.35 | 1.9 | 238.4 | 242 | 0.28 | 0.29 | 238.8 | 242.8 | 0 | 0 | 239.3 | 242
2026-08-26 | 00:00:00 | 0.9 | 4.2 | 238.22 | 243.48 | 1.3 | 5.91 | 238.3 | 243 | 0.29 | 0.67 | 238.5 | 243.4 | 0 | 0 | 236.7 | 242.3
2026-08-26 | 01:00:00 | 0.8 | 2.3 | 238.42 | 243.19 | 1.44 | 1.82 | 237.1 | 242.8 | 0.54 | 0.57 | 238.9 | 243.2 | 0 | 0 | 236.7 | 242
2026-08-26 | 02:00:00 | 0.8 | 3.6 | 238.02 | 243.38 | 1.44 | 1.98 | 238.4 | 242.9 | 0.53 | 0.55 | 238.6 | 243.7 | 0 | 0 | 236.4 | 242
2026-08-26 | 03:00:00 | 0.8 | 3.2 | 238.02 | 241.8 | 1.43 | 1.85 | 238.8 | 241.2 | 0.52 | 0.54 | 238.8 | 242.2 | 0 | 0 | 239.3 | 240.4
2026-08-26 | 04:00:00 | 0.9 | 12.3 | 229.78 | 244.28 | 1.45 | 1.98 | 231.4 | 243.5 | 0.52 | 0.54 | 231.6 | 243.9 | 0 | 0 | 233.4 | 241.7
2026-08-26 | 05:00:00 | 0.9 | 11.8 | 219.06 | 246.07 | 1.32 | 12.61 | 214.3 | 245.9 | 0.3 | 11.71 | 214.3 | 246 | 0 | 0 | 213.5 | 242.6
2026-08-26 | 06:00:00 | 0.9 | 12.5 | 218.26 | 237.82 | 1.51 | 16.69 | 215.9 | 237.1 | 0.3 | 1.1 | 217 | 237.5 | 0 | 0 | 217.7 | 237.2
2026-08-26 | 07:00:00 | 1 | 13.1 | 220.15 | 242.19 | 1.59 | 12.76 | 219.2 | 241.7 | 0.3 | 12.72 | 218.6 | 241.3 | 0 | 0 | 216.8 | 241.1
2026-08-26 | 08:00:00 | 1.2 | 20.6 | 209.72 | 239.11 | 1.79 | 5.81 | 213 | 238.1 | 0.55 | 3.11 | 213.2 | 238.6 | 0 | 0 | 213 | 236.4
2026-08-26 | 09:00:00 | 1.2 | 12.9 | 213.69 | 240.11 | 1.54 | 10.3 | 215.8 | 238.3 | 0.55 | 8.96 | 215.3 | 238.6 | 0 | 0 | 216.3 | 237.9
2026-08-26 | 10:00:00 | 1.2 | 12.6 | 210.22 | 237.53 | 1.44 | 2.02 | 213.7 | 236.6 | 0.55 | 0.72 | 212.6 | 236.8 | 0 | 0 | 211.8 | 235.3
2026-08-26 | 11:00:00 | 0.9 | 12.5 | 213.5 | 241.2 | 1.67 | 7.58 | 216 | 240 | 0.68 | 6.91 | 215.2 | 239.9 | 0 | 0 | 216.1 | 239.9
2026-08-26 | 12:00:00 | 1.1 | 3.6 | 219.65 | 241.6 | 1.76 | 13.61 | 217.6 | 240.9 | 0.69 | 1.32 | 218.3 | 240.6 | 0 | 0 | 218 | 239.6
2026-08-26 | 13:00:00 | 1.1 | 3.3 | 230.38 | 243.09 | 1.58 | 9.76 | 229.3 | 242.5 | 0.58 | 0.7 | 229.6 | 242.9 | 0 | 0 | 232.8 | 243.5
2026-08-26 | 14:00:00 | 1 | 13.2 | 230.57 | 242.19 | 1.64 | 3.86 | 230.1 | 240.9 | 0.53 | 0.58 | 231.7 | 241.1 | 0 | 0 | 229 | 241.4
2026-08-26 | 15:00:00 | 1.5 | 23.5 | 215.78 | 241.3 | 3.14 | 8.92 | 216.7 | 240.1 | 0.32 | 0.87 | 217.2 | 240.1 | 0 | 0 | 218 | 238.5
2026-08-26 | 16:00:00 | 2.1 | 14 | 196.81 | 235.54 | 3.39 | 19.47 | 198.9 | 231.6 | 0.61 | 6.75 | 199.8 | 231.1 | 0 | 0 | 198.3 | 229.8
2026-08-26 | 17:00:00 | 2.3 | 16.2 | 201.78 | 235.74 | 3.68 | 16.5 | 201.4 | 234.2 | 0.77 | 1.25 | 202 | 234.3 | 0 | 0 | 201 | 234.2
2026-08-26 | 18:00:00 | 2.1 | 16.4 | 209.13 | 234.45 | 2.36 | 16.5 | 209.4 | 232.2 | 0.84 | 1.16 | 209.7 | 232 | 0 | 0 | 209.8 | 231.7
2026-08-26 | 19:00:00 | 1.5 | 13.7 | 218.06 | 241.7 | 2.46 | 3.77 | 219.1 | 239 | 0.79 | 1.38 | 219.5 | 239.2 | 0 | 0 | 218.7 | 238.9
2026-08-26 | 20:00:00 | 1.4 | 5 | 231.77 | 241.4 | 2.48 | 15.5 | 228.6 | 240.9 | 0.64 | 1.39 | 228.6 | 240.8 | 0 | 0 | 228.7 | 241.6
2026-08-26 | 21:00:00 | 1.3 | 4.4 | 233.45 | 242.59 | 1.85 | 5.14 | 234 | 242 | 0.52 | 0.71 | 235.4 | 241.8 | 0 | 0 | 235.6 | 241.6
2026-08-26 | 22:00:00 | 1.1 | 2.3 | 231.57 | 242.19 | 1.54 | 2.27 | 233.3 | 241.8 | 0.52 | 0.53 | 234.1 | 241.3 | 0 | 0 | 234.2 | 241.1
2026-08-26 | 23:00:00 | 1.2 | 4.1 | 224.22 | 239.81 | 1.47 | 1.92 | 226.3 | 240.2 | 0.52 | 0.55 | 226.5 | 240.4 | 0 | 0 | 227.6 | 239.3
2026-08-27 | 00:00:00 | 1 | 2.9 | 237.03 | 241.6 | 1.48 | 6.55 | 237.4 | 241.3 | 0.52 | 0.53 | 236.9 | 241.4 | 0 | 0 | 237.3 | 239.9
2026-08-27 | 01:00:00 | 0.9 | 4.1 | 236.73 | 242.09 | 1.33 | 1.92 | 237.3 | 242.1 | 0.28 | 0.53 | 236.7 | 242.1 | 0 | 0 | 234.1 | 240.5
2026-08-27 | 02:00:00 | 0.9 | 2.4 | 234.25 | 242.29 | 1.31 | 5.34 | 235.7 | 241.4 | 0.28 | 0.31 | 235.7 | 241.5 | 0 | 0 | 239.3 | 240.5
2026-08-27 | 03:00:00 | 0.9 | 2.6 | 234.84 | 241.89 | 1.3 | 1.7 | 234.9 | 242 | 0.28 | 1.29 | 233.9 | 241.9 | 0 | 0 | 235 | 240.5
2026-08-27 | 04:00:00 | 1 | 13.8 | 230.08 | 244.58 | 1.46 | 2.12 | 228.5 | 244.2 | 0.56 | 0.6 | 237.4 | 244.5 | 0 | 0 | 229 | 240.5
2026-08-27 | 05:00:00 | 1.3 | 12.6 | 229.68 | 250.83 | 1.64 | 13.34 | 227.8 | 249.6 | 0.57 | 0.94 | 231.8 | 241.1 | 0 | 0 | 227.6 | 250
2026-08-27 | 06:00:00 | 1 | 12.7 | 225.61 | 240.8 | 1.47 | 13.12 | 223.2 | 240 | 0.58 | 1.26 | 229 | 239.8 | 0 | 0 | 223.2 | 239.3
2026-08-27 | 07:00:00 | 1 | 21.2 | 216.77 | 243.38 | 1.51 | 17.17 | 223.1 | 242.9 | 0.53 | 4.63 | 223.9 | 239.7 | 0 | 0 | 218.2 | 242.6
2026-08-27 | 08:00:00 | 1 | 12.4 | 223.43 | 241.4 | 1.74 | 2.55 | 224.3 | 240.9 | 0.52 | 0.97 | 225 | 240.6 | 0 | 0 | 222.4 | 240.5
2026-08-27 | 09:00:00 | 1.2 | 10.3 | 211.41 | 242.29 | 2.1 | 14.1 | 216.1 | 241.6 | 0.53 | 0.83 | 217.5 | 241.5 | 0 | 0 | 217 | 239
2026-08-27 | 10:00:00 | 0.9 | 2.6 | 220.35 | 242.69 | 1.78 | 10.28 | 221.3 | 242.2 | 0.31 | 0.55 | 220.4 | 242.5 | 0 | 0 | 223 | 241.7
2026-08-27 | 11:00:00 | 0.9 | 3.8 | 227.2 | 242.99 | 1.46 | 12.93 | 228.1 | 242.4 | 0.3 | 6.6 | 227.8 | 242 | 0 | 0 | 228.2 | 242.5
2026-08-27 | 12:00:00 | 0.9 | 3.7 | 223.62 | 247.16 | 1.58 | 2.57 | 225.4 | 246.2 | 0.58 | 1.88 | 225.6 | 246.7 | 0 | 0 | 225.5 | 245.3
2026-08-27 | 13:00:00 | 1.2 | 12.9 | 218.76 | 241.6 | 1.54 | 10.13 | 216.2 | 240.5 | 0.56 | 9.55 | 217.3 | 241.1 | 0 | 0 | 216.7 | 241.4
2026-08-27 | 14:00:00 | 1.3 | 13.4 | 224.52 | 241.7 | 1.55 | 12.94 | 225.2 | 240.6 | 0.54 | 0.59 | 225.7 | 240.7 | 0 | 0 | 218.7 | 239.6
2026-08-27 | 15:00:00 | 1.6 | 12.9 | 215.98 | 238.22 | 2.19 | 10.28 | 210.6 | 237.6 | 0.59 | 8.18 | 210.7 | 237.2 | 0 | 0 | 210.5 | 235.3
2026-08-27 | 16:00:00 | 2.2 | 31.5 | 196.02 | 233.55 | 2.61 | 17.09 | 196.8 | 230.4 | 0.92 | 1.72 | 196.6 | 231.3 | 0 | 0 | 196.7 | 230.3
2026-08-27 | 17:00:00 | 6.9 | 19.2 | 206.94 | 234.15 | 2.41 | 21.12 | 204.1 | 235 | 0.86 | 1.17 | 204.1 | 234.8 | 0 | 0 | 206 | 231.7
2026-08-27 | 18:00:00 | 2.1 | 19.2 | 214.19 | 238.02 | 2.42 | 3.85 | 213.9 | 238.2 | 0.92 | 1.14 | 214.2 | 237.7 | 0 | 0 | 213.9 | 237.3
2026-08-27 | 19:00:00 | 1.8 | 13.4 | 217.07 | 236.83 | 2.49 | 13.65 | 216.4 | 236.3 | 0.92 | 1.24 | 216.9 | 235.9 | 0 | 0 | 214.7 | 234.2
2026-08-27 | 20:00:00 | 2 | 3 | 224.82 | 239.91 | 1.83 | 3.92 | 222.9 | 239.5 | 0.38 | 1.14 | 223.7 | 239.4 | 0 | 0 | 223.7 | 239.3
2026-08-27 | 21:00:00 | 1.6 | 5 | 230.67 | 242.19 | 1.69 | 7.34 | 228.2 | 241.3 | 0.28 | 0.44 | 229.8 | 241.6 | 0 | 0 | 231 | 238.7
2026-08-27 | 22:00:00 | 1.2 | 2 | 232.36 | 242.49 | 1.5 | 2.01 | 234.1 | 241.8 | 0.28 | 0.31 | 233.4 | 241.9 | 0 | 0 | 233.9 | 239.3
2026-08-27 | 23:00:00 | 1 | 2 | 232.96 | 241.3 | 1.5 | 1.99 | 234.6 | 240.7 | 0.3 | 0.7 | 235.6 | 240.9 | 0 | 0 | 233.3 | 239.9
2026-08-28 | 00:00:00 | 1 | 2.6 | 229.38 | 243.19 | 1.37 | 1.99 | 231.6 | 242.3 | 0.53 | 0.58 | 231.9 | 242.6 | 0 | 0 | 234.2 | 240.5
2026-08-28 | 01:00:00 | 0.9 | 3.6 | 237.62 | 242.59 | 1.37 | 1.98 | 235.7 | 242.2 | 0.28 | 0.54 | 237.6 | 242.4 | 0 | 0 | 238.7 | 240.5
2026-08-28 | 02:00:00 | 1 | 2.6 | 237.62 | 243.58 | 1.24 | 1.65 | 238.6 | 243.2 | 0.28 | 0.29 | 239.3 | 242.8 | 0 | 0 | 236.7 | 242
2026-08-28 | 03:00:00 | 0.9 | 1.5 | 240.8 | 244.48 | 1.26 | 1.89 | 241.1 | 244.3 | 0.28 | 0.29 | 241.5 | 243.9 | 0 | 0 | 242 | 242.6
2026-08-28 | 04:00:00 | 0.9 | 12.4 | 229.58 | 242.59 | 1.26 | 5.33 | 227.1 | 242.3 | 0.28 | 6.92 | 228.9 | 242.6 | 0 | 0 | 226.8 | 242.6
2026-08-28 | 05:00:00 | 1.2 | 12.9 | 228.59 | 244.28 | 1.41 | 13.18 | 226.9 | 244.1 | 0.54 | 12.16 | 226.3 | 243.9 | 0 | 0 | 226.4 | 243.8
2026-08-28 | 06:00:00 | 1 | 16.5 | 207.64 | 239.21 | 1.73 | 13.36 | 207.9 | 238.5 | 0.54 | 6.76 | 208.7 | 239 | 0 | 0 | 203 | 238.7
2026-08-28 | 07:00:00 | 1.6 | 27.9 | 203.27 | 242.29 | 1.61 | 9.43 | 210.6 | 241.8 | 0.32 | 4.22 | 212.1 | 241 | 0 | 0 | 211.2 | 241.4
2026-08-28 | 08:00:00 | 1.2 | 20.1 | 224.72 | 252.92 | 1.27 | 2.37 | 226.9 | 252.5 | 0.31 | 0.73 | 227.3 | 251.6 | 0 | 0 | 227.4 | 247.3
2026-08-28 | 09:00:00 | 0.9 | 3.9 | 224.22 | 252.42 | 1.73 | 16.99 | 223.8 | 252.1 | 0.31 | 6.88 | 225.5 | 251.8 | 0 | 0 | 223.2 | 250.7
2026-08-28 | 10:00:00 | 0.9 | 3.6 | 222.93 | 241.1 | 2.02 | 8.38 | 224.3 | 240.4 | 0.55 | 6.84 | 221.7 | 240.5 | 0 | 0 | 223.7 | 238.2
2026-08-28 | 11:00:00 | 1.1 | 12.3 | 221.04 | 244.48 | 2.27 | 6.25 | 225 | 243.3 | 1.02 | 1.08 | 225.1 | 242.6 | 0 | 0 | 226.3 | 241.7
2026-08-28 | 12:00:00 | 1.5 | 13.9 | 224.42 | 244.08 | 2.22 | 10.41 | 225.3 | 242.7 | 1.02 | 1.06 | 225.4 | 242.9 | 0 | 0 | 226 | 243.2
2026-08-28 | 13:00:00 | 1.4 | 23.6 | 213.5 | 247.16 | 1.62 | 9.8 | 216.7 | 244.4 | 0.52 | 1.04 | 218.7 | 244.4 | 0 | 0 | 218.2 | 245.9
2026-08-28 | 14:00:00 | 1.5 | 15.2 | 220.84 | 242.29 | 1.79 | 11.09 | 223.2 | 241.3 | 0.56 | 9.89 | 225.2 | 241.6 | 0 | 0 | 223.2 | 242
2026-08-28 | 15:00:00 | 1.4 | 33.9 | 201.58 | 241.89 | 2.16 | 10.83 | 207 | 240.4 | 0.84 | 10.04 | 206.1 | 239.5 | 0 | 0 | 206.3 | 239.3
2026-08-28 | 16:00:00 | 2 | 17.2 | 199.99 | 236.33 | 2.53 | 20.87 | 202.5 | 236.8 | 0.78 | 5.08 | 202.8 | 235.5 | 0 | 0 | 202.6 | 235.6
2026-08-28 | 17:00:00 | 1.8 | 13.6 | 207.64 | 242.79 | 1.81 | 4.64 | 209.9 | 242.8 | 0.56 | 0.81 | 211.9 | 242 | 0 | 0 | 210.7 | 242.3
2026-08-28 | 18:00:00 | 1.8 | 13.4 | 224.62 | 240.7 | 1.92 | 6.48 | 224.8 | 240.5 | 0.55 | 0.7 | 224.7 | 240.7 | 0 | 0 | 224.5 | 238.7
2026-08-28 | 19:00:00 | 1.3 | 14.2 | 224.91 | 239.41 | 1.9 | 2.73 | 227.9 | 239.3 | 0.59 | 1.17 | 228.2 | 239.6 | 0 | 0 | 226.5 | 238.7
2026-08-28 | 20:00:00 | 1.8 | 5 | 224.91 | 235.64 | 2.28 | 3.04 | 222.2 | 233 | 0.68 | 1.5 | 222.7 | 233.9 | 0 | 0 | 229.5 | 234.7
2026-08-28 | 21:00:00 | 1.4 | 3.9 | 227.1 | 242.99 | 1.8 | 5.57 | 227.3 | 241.2 | 0.53 | 0.89 | 228.1 | 241.7 | 0 | 0 | 229 | 240.5
2026-08-28 | 22:00:00 | 1.1 | 4.3 | 233.45 | 239.11 | 1.44 | 5.48 | 232 | 238.9 | 0.52 | 0.54 | 231.7 | 239.1 | 0 | 0 | 229 | 241.1
2026-08-28 | 23:00:00 | 1 | 4 | 231.96 | 240.21 | 1.36 | 1.9 | 233.2 | 240.3 | 0.52 | 0.52 | 235 | 239.9 | 0 | 0 | 235.8 | 237.3
2026-08-29 | 00:00:00 | 1 | 4 | 233.45 | 242.29 | 1.42 | 4.04 | 235.6 | 242 | 0.51 | 0.52 | 235.8 | 242.2 | 0 | 0 | 237 | 242.6
2026-08-29 | 01:00:00 | 0.8 | 3.5 | 237.43 | 242.89 | 1.23 | 1.71 | 236.9 | 242.4 | 0.28 | 0.52 | 236.8 | 242.6 | 0 | 0 | 238.2 | 240.8
2026-08-29 | 02:00:00 | 0.9 | 3.7 | 237.92 | 241.99 | 1.22 | 1.6 | 238.2 | 241.8 | 0.28 | 0.29 | 239.6 | 241.9 | 0 | 0 | 235 | 240.5
2026-08-29 | 03:00:00 | 0.9 | 4 | 237.62 | 243.78 | 1.21 | 4.64 | 237.6 | 243.4 | 0.28 | 0.63 | 238.5 | 243.7 | 0 | 0 | 239.9 | 241.5
2026-08-29 | 04:00:00 | 0.9 | 12.6 | 232.96 | 244.48 | 1.37 | 7.1 | 233.9 | 244.2 | 0.55 | 0.57 | 233.2 | 244.4 | 0 | 0 | 233.9 | 241.5
2026-08-29 | 05:00:00 | 1.1 | 13.2 | 227.79 | 242.79 | 1.63 | 13.67 | 223.3 | 241.9 | 0.55 | 12.77 | 223.3 | 242.2 | 0 | 0 | 224.5 | 242
2026-08-29 | 06:00:00 | 1 | 13.1 | 218.06 | 242.89 | 1.71 | 4 | 221.7 | 242.6 | 0.38 | 1.07 | 221.7 | 242.4 | 0 | 0 | 220.9 | 242
2026-08-29 | 07:00:00 | 1.3 | 12.5 | 213.4 | 241.99 | 1.38 | 14.67 | 215.1 | 241.2 | 0.29 | 9.71 | 215.6 | 241.7 | 0 | 0 | 215.2 | 238.7
2026-08-29 | 08:00:00 | 1 | 12.2 | 228.49 | 250.73 | 1.33 | 5.47 | 228.1 | 249.9 | 0.3 | 3.47 | 228.4 | 250 | 0 | 0 | 227.1 | 246.6
2026-08-29 | 09:00:00 | 1.1 | 21.1 | 214.19 | 246.76 | 1.81 | 8.16 | 216.7 | 244.9 | 0.53 | 2.76 | 216.6 | 245.9 | 0 | 0 | 216.2 | 243.7
2026-08-29 | 10:00:00 | 1.2 | 2.1 | 222.13 | 245.77 | 1.67 | 4.05 | 222.6 | 245.1 | 0.52 | 0.57 | 222.6 | 245 | 0 | 0 | 224.6 | 243.2
2026-08-29 | 11:00:00 | 1 | 13.2 | 214.79 | 242.69 | 1.45 | 7.32 | 217.8 | 241.8 | 0.35 | 4.01 | 222.1 | 240.1 | 0 | 0 | 217.3 | 243.1
2026-08-29 | 12:00:00 | 1 | 14.5 | 217.67 | 247.36 | 1.41 | 2.83 | 222.1 | 246.9 | 0.3 | 4.01 | 226.9 | 241.8 | 0 | 0 | 225.6 | 245.3
2026-08-29 | 13:00:00 | 1 | 24.3 | 221.34 | 248.85 | 1.55 | 2.48 | 223.7 | 248.1 | 0.29 | 8.96 | 224.2 | 248.4 | 0 | 0 | 226.8 | 247.8
2026-08-29 | 14:00:00 | 1.5 | 19.1 | 223.33 | 244.48 | 1.63 | 2.51 | 224.6 | 244.1 | 0.53 | 1.07 | 224.2 | 243.7 | 0 | 0 | 226.8 | 244.9
2026-08-29 | 15:00:00 | 2.1 | 14 | 220.15 | 246.07 | 1.91 | 3.23 | 219.2 | 244.8 | 0.82 | 1.09 | 220.1 | 244.9 | 0 | 0 | 217.6 | 245.6
2026-08-29 | 16:00:00 | 2.1 | 31.2 | 202.47 | 238.32 | 2.02 | 16.69 | 212.3 | 237.7 | 0.82 | 1.86 | 212.4 | 237.4 | 0 | 0 | 212.1 | 238.4
2026-08-29 | 17:00:00 | 2.5 | 17.3 | 207.83 | 240.21 | 2.06 | 2.86 | 213 | 240.2 | 0.85 | 1.7 | 212.9 | 240.2 | 0 | 0 | 213.7 | 239.9
2026-08-29 | 18:00:00 | 2 | 18.2 | 215.28 | 239.81 | 1.89 | 8.41 | 218.4 | 239.6 | 0.83 | 1 | 218.6 | 239.8 | 0 | 0 | 219.2 | 239.9
2026-08-29 | 19:00:00 | 2.6 | 25.8 | 220.15 | 243.88 | 2.03 | 6.56 | 225.9 | 243.6 | 0.81 | 1.63 | 226.5 | 243.5 | 0 | 0 | 228.1 | 244.3
2026-08-29 | 20:00:00 | 2 | 13.5 | 231.57 | 246.46 | 2.03 | 6.1 | 234 | 246 | 0.78 | 1.48 | 235 | 244.7 | 0 | 0 | 232.5 | 245.9
2026-08-29 | 21:00:00 | 1.3 | 4.1 | 239.02 | 246.16 | 1.25 | 2.28 | 238.8 | 246 | 0.29 | 0.85 | 240 | 245.9 | 0 | 0 | 239.9 | 245.9
2026-08-29 | 22:00:00 | 1.1 | 4.1 | 233.45 | 242.99 | 1.26 | 1.72 | 233.6 | 242.6 | 0.28 | 0.3 | 233.8 | 242.8 | 0 | 0 | 233.3 | 240.8
2026-08-29 | 23:00:00 | 0.9 | 3.1 | 232.86 | 243.38 | 1.25 | 5.89 | 234.8 | 242.8 | 0.28 | 0.3 | 234.8 | 243.3 | 0 | 0 | 234.4 | 239.7
2026-08-30 | 00:00:00 | 0.9 | 3 | 232.56 | 241.6 | 1.26 | 6.32 | 234.1 | 241 | 0.29 | 0.67 | 232.8 | 240.4 | 0 | 0 | 233 | 239.9
2026-08-30 | 01:00:00 | 0.8 | 2.6 | 236.93 | 241.4 | 1.33 | 6.44 | 236.4 | 241.5 | 0.52 | 0.56 | 236.6 | 241.1 | 0 | 0 | 238.2 | 239.8
2026-08-30 | 02:00:00 | 0.8 | 1.7 | 237.82 | 242.39 | 1.34 | 6.55 | 238.1 | 243.1 | 0.52 | 0.53 | 237.8 | 241.5 | 0 | 0 | 239.8 | 240.5
2026-08-30 | 03:00:00 | 0.8 | 2.1 | 237.92 | 242.69 | 1.34 | 1.78 | 239.4 | 242.8 | 0.51 | 0.52 | 239.1 | 242.6 | 0 | 0 | 240.2 | 241.4
2026-08-30 | 04:00:00 | 0.8 | 3.5 | 232.56 | 242.69 | 1.25 | 6.4 | 231.9 | 242.4 | 0.28 | 0.52 | 232.2 | 242.4 | 0 | 0 | 231.9 | 242
2026-08-30 | 05:00:00 | 0.9 | 13.1 | 226.6 | 243.09 | 1.28 | 12.64 | 227.5 | 242.6 | 0.28 | 11.84 | 228.9 | 242.9 | 0 | 0 | 227.1 | 240.8
2026-08-30 | 06:00:00 | 0.9 | 12.2 | 226.8 | 241.8 | 1.3 | 5.82 | 226 | 241.3 | 0.33 | 0.9 | 226.2 | 241.7 | 0 | 0 | 227.5 | 240.8
2026-08-30 | 07:00:00 | 1 | 23 | 217.76 | 249.54 | 1.31 | 13.99 | 218.6 | 248.2 | 0.32 | 9.54 | 222.5 | 249.1 | 0 | 0 | 218.5 | 249.4
2026-08-30 | 08:00:00 | 1 | 24 | 217.96 | 247.95 | 1.45 | 20.4 | 223.3 | 247.6 | 0.53 | 2.38 | 221.9 | 247.5 | 0 | 0 | 222.7 | 245.6
2026-08-30 | 09:00:00 | 1.5 | 28 | 212.3 | 248.15 | 1.68 | 12.73 | 214 | 247.2 | 0.52 | 0.56 | 214 | 247.5 | 0 | 0 | 216.1 | 247.2
2026-08-30 | 10:00:00 | 1.8 | 38.2 | 194.63 | 239.51 | 1.81 | 12.68 | 203.2 | 241.9 | 0.53 | 0.57 | 204.4 | 239.9 | 0 | 0 | 204.7 | 242
2026-08-30 | 11:00:00 | 1.3 | 27.2 | 214.09 | 243.98 | 1.44 | 8.39 | 216.7 | 244.2 | 0.52 | 6.73 | 219.7 | 244.1 | 0 | 0 | 220.4 | 241.7
2026-08-30 | 12:00:00 | 1.3 | 16.1 | 224.22 | 247.06 | 1.24 | 2.14 | 225.8 | 246.3 | 0.3 | 0.79 | 226.7 | 246.6 | 0 | 0 | 229.5 | 246.3
2026-08-30 | 13:00:00 | 1.4 | 19.3 | 220.05 | 243.68 | 1.43 | 10.26 | 224.1 | 242.9 | 0.55 | 9.35 | 224.6 | 243.3 | 0 | 0 | 226.6 | 242.3
2026-08-30 | 14:00:00 | 1.4 | 2.6 | 223.52 | 244.28 | 1.62 | 11.24 | 227.3 | 244.1 | 0.66 | 9.83 | 226.5 | 244.2 | 0 | 0 | 227.4 | 244.4
2026-08-30 | 15:00:00 | 1.6 | 12.5 | 217.37 | 244.58 | 1.87 | 21.62 | 217.1 | 244.4 | 0.83 | 20.52 | 214.7 | 244.3 | 0 | 0 | 218.2 | 242.6
2026-08-30 | 16:00:00 | 1.5 | 2.2 | 220.45 | 243.78 | 1.87 | 7.55 | 221.4 | 242.1 | 0.81 | 1.42 | 221.5 | 242.6 | 0 | 0 | 222.2 | 242.6
2026-08-30 | 17:00:00 | 1.4 | 13.6 | 219.85 | 247.85 | 1.82 | 7.07 | 222.5 | 247.7 | 0.8 | 1.08 | 222.9 | 247.7 | 0 | 0 | 222.2 | 248.1
2026-08-30 | 18:00:00 | 2.1 | 11.3 | 223.13 | 244.68 | 1.78 | 2.59 | 225.3 | 247.7 | 0.8 | 1.14 | 225.6 | 246.3 | 0 | 0 | 225 | 248.1
2026-08-30 | 19:00:00 | 1.7 | 15.3 | 223.23 | 239.21 | 2.21 | 7.08 | 227.4 | 239.6 | 1.09 | 1.66 | 226.6 | 239.7 | 0 | 0 | 226.6 | 240.5
2026-08-30 | 20:00:00 | 2.1 | 14.1 | 218.46 | 240.31 | 1.9 | 2.78 | 223.5 | 240.2 | 0.37 | 1.13 | 226.2 | 240.2 | 0 | 0 | 222.2 | 238.7
2026-08-30 | 21:00:00 | 1.3 | 3.2 | 222.13 | 243.09 | 1.46 | 2.17 | 224.3 | 242.6 | 0.28 | 0.43 | 224.6 | 243.2 | 0 | 0 | 228.4 | 239.6
2026-08-30 | 22:00:00 | 1.2 | 3.2 | 238.92 | 245.77 | 1.4 | 6.15 | 238.8 | 246.2 | 0.28 | 1.37 | 239.8 | 246.2 | 0 | 0 | 239.6 | 245.3
2026-08-30 | 23:00:00 | 0.9 | 1.9 | 239.11 | 249.84 | 1.37 | 1.96 | 239.2 | 249.3 | 0.55 | 0.64 | 240.5 | 249 | 0 | 0 | 237.9 | 248.8
2026-08-31 | 00:00:00 | 1 | 4.3 | 238.42 | 243.19 | 1.32 | 1.73 | 237.8 | 242.9 | 0.53 | 0.56 | 239.4 | 243.5 | 0 | 0 | 240.2 | 241.1
2026-08-31 | 01:00:00 | 0.8 | 2 | 237.53 | 246.26 | 1.19 | 1.62 | 237.2 | 246.1 | 0.28 | 0.53 | 238.8 | 246.6 | 0 | 0 | 234.4 | 245.3
2026-08-31 | 02:00:00 | 0.8 | 4 | 241.1 | 246.36 | 1.24 | 5.94 | 241 | 245.8 | 0.28 | 0.3 | 241.9 | 246 | 0 | 0 | 238.7 | 245.3
2026-08-31 | 03:00:00 | 0.8 | 1.7 | 237.82 | 247.26 | 1.2 | 1.73 | 238.1 | 246.3 | 0.29 | 0.69 | 237.4 | 246.8 | 0 | 0 | 238.7 | 245.2
2026-08-31 | 04:00:00 | 0.8 | 3.5 | 237.72 | 245.97 | 1.37 | 1.81 | 236.3 | 245.7 | 0.54 | 0.57 | 236.2 | 245.9 | 0 | 0 | 235.9 | 243.5
2026-08-31 | 05:00:00 | 0.9 | 3.9 | 225.71 | 245.27 | 1.23 | 12.53 | 221.5 | 244.9 | 0.31 | 11.91 | 220.9 | 244.5 | 0 | 0 | 220.7 | 242.9
2026-08-31 | 06:00:00 | 0.8 | 11.9 | 227.6 | 247.16 | 1.24 | 12.84 | 222.3 | 246.6 | 0.3 | 1.1 | 227.9 | 246.8 | 0 | 0 | 222.2 | 247.2
2026-08-31 | 07:00:00 | 0.8 | 12.7 | 219.25 | 249.64 | 1.34 | 9.61 | 221.1 | 248.8 | 0.3 | 6.56 | 221.5 | 248.9 | 0 | 0 | 221.5 | 250.7
2026-08-31 | 08:00:00 | 1 | 16.4 | 218.56 | 251.82 | 1.71 | 9.83 | 223.5 | 251.2 | 0.53 | 0.62 | 222.1 | 251.6 | 0 | 0 | 223.4 | 251.6
2026-08-31 | 09:00:00 | 1.3 | 13.3 | 214.79 | 252.52 | 1.65 | 5.39 | 221.9 | 251.1 | 0.31 | 0.6 | 223.9 | 251 | 0 | 0 | 221.2 | 251.3
2026-08-31 | 10:00:00 | 1.1 | 13.1 | 220.64 | 247.95 | 1.71 | 14.23 | 224.3 | 245.5 | 0.32 | 6.7 | 224.2 | 245.9 | 0 | 0 | 223.7 | 249.4
2026-08-31 | 11:00:00 | 1.2 | 6.9 | 223.72 | 244.48 | 1.41 | 10.13 | 221.9 | 242.3 | 0.46 | 9.34 | 220.9 | 242.6 | 0 | 0 | 220.9 | 241.6
2026-08-31 | 12:00:00 | 1 | 1.9 | 225.41 | 246.46 | 1.54 | 10.52 | 223.3 | 246.8 | 0.62 | 9.71 | 222.8 | 245.7 | 0 | 0 | 225.3 | 245.6
2026-08-31 | 13:00:00 | 1.2 | 12.9 | 201.38 | 238.22 | 1.27 | 9.73 | 206.6 | 236 | 0.57 | 8.96 | 207.8 | 237.2 | 0 | 0 | 208.2 | 236.7
2026-08-31 | 14:00:00 | 1.6 | 13 | 220.35 | 242.59 | 1.62 | 10.21 | 220.4 | 241.9 | 0.55 | 9.37 | 221.2 | 241.8 | 0 | 0 | 219.9 | 241.1
2026-08-31 | 15:00:00 | 1.5 | 3.6 | 221.74 | 242.99 | 1.59 | 10.48 | 218.2 | 242.3 | 0.55 | 9.36 | 217.9 | 241.7 | 0 | 0 | 218.2 | 242.8
2026-08-31 | 16:00:00 | 2 | 14.1 | 216.67 | 240.31 | 2.07 | 2.86 | 212.3 | 239.6 | 1.08 | 1.22 | 214 | 239.6 | 0 | 0 | 213.7 | 237.4
2026-08-31 | 17:00:00 | 2 | 10.7 | 213.3 | 238.32 | 2.17 | 3.59 | 212.9 | 239.1 | 0.84 | 1.31 | 212.9 | 239.3 | 0 | 0 | 210.9 | 238.7
2026-08-31 | 18:00:00 | 1.6 | 12.8 | 210.62 | 240.01 | 2.38 | 10.64 | 211.8 | 239.2 | 0.55 | 0.92 | 210.9 | 239 | 0 | 0 | 211.2 | 236.7
2026-08-31 | 19:00:00 | 1.3 | 3.9 | 227.79 | 242.59 | 2.15 | 6.32 | 226.1 | 241.5 | 0.64 | 1.07 | 226.5 | 241.4 | 0 | 0 | 227.1 | 241.4
2026-08-31 | 20:00:00 | 2 | 14.3 | 225.91 | 240.7 | 2.51 | 3.38 | 225.8 | 240.8 | 0.39 | 1.19 | 226.1 | 240.9 | 0 | 0 | 227.1 | 240.5
2026-08-31 | 21:00:00 | 1.5 | 3.1 | 233.95 | 248.05 | 1.72 | 2.63 | 234.9 | 248 | 0.36 | 0.75 | 236.5 | 248.3 | 0 | 0 | 235 | 243.2
2026-08-31 | 22:00:00 | 1.2 | 1.8 | 239.21 | 245.17 | 1.41 | 5.38 | 239.2 | 245.6 | 0.52 | 0.56 | 239.2 | 244.8 | 0 | 0 | 235 | 242.6
2026-08-31 | 23:00:00 | 1 | 3.3 | 238.12 | 244.48 | 1.28 | 1.71 | 238.6 | 244.3 | 0.28 | 0.53 | 238.5 | 244.2 | 0 | 0 | 240.8 | 242.6
2026-09-01 | 00:00:00 | 0.9 | 2.4 | 239.21 | 243.68 | 1.21 | 1.6 | 239.6 | 243.3 | 0.28 | 0.3 | 239.8 | 243.4 | 0 | 0 | 239.3 | 242.6
2026-09-01 | 01:00:00 | 0.8 | 3.4 | 240.8 | 244.87 | 1.25 | 1.59 | 241.2 | 244.9 | 0.28 | 0.32 | 241.5 | 244.4 | 0 | 0 | 239.3 | 243.5
2026-09-01 | 02:00:00 | 0.8 | 3.2 | 239.31 | 245.27 | 1.38 | 1.78 | 238.9 | 244.3 | 0.3 | 0.66 | 239 | 243.8 | 0 | 0 | 241 | 243.5
2026-09-01 | 03:00:00 | 0.8 | 3.5 | 239.81 | 244.38 | 1.34 | 1.74 | 240 | 245 | 0.28 | 0.56 | 240.3 | 244.4 | 0 | 0 | 242.1 | 242.6
2026-09-01 | 04:00:00 | 1 | 3 | 230.67 | 244.87 | 1.23 | 1.6 | 228.3 | 244.7 | 0.28 | 0.3 | 228.7 | 245.2 | 0 | 0 | 230.7 | 242.1
2026-09-01 | 05:00:00 | 0.9 | 12.3 | 229.78 | 250.14 | 1.41 | 13.71 | 226.1 | 249.3 | 0.28 | 12.91 | 226.2 | 250 | 0 | 0 | 227.4 | 249.4
2026-09-01 | 06:00:00 | 0.9 | 12.4 | 223.92 | 241.8 | 1.64 | 13.68 | 226.4 | 241.1 | 0.39 | 1.57 | 226.2 | 241.3 | 0 | 0 | 225 | 240.4
2026-09-01 | 07:00:00 | 0.9 | 13 | 226.7 | 243.88 | 1.69 | 13.07 | 228.5 | 243 | 0.3 | 12.05 | 229 | 243.2 | 0 | 0 | 228 | 242.3
2026-09-01 | 08:00:00 | 1.2 | 12.5 | 225.01 | 245.67 | 2.35 | 2.58 | 238.5 | 238.9 | 0.3 | 0.78 | 223.5 | 245.2 | 0 | 0 | 221.2 | 245
2026-09-01 | 09:00:00 | 1.3 | 14.1 | 213 | 241.99 | 1.67 | 2.59 | 228.8 | 238.9 | 0.3 | 0.32 | 214.2 | 241.3 | 0 | 0 | 210.7 | 239.3
2026-09-01 | 10:00:00 | 1.2 | 13.4 | 208.53 | 241.6 | 1.61 | 10.66 | 227.3 | 237.5 | 0.31 | 6.78 | 208.6 | 240.8 | 0 | 0 | 208.7 | 239.2
2026-09-01 | 11:00:00 | 1.3 | 18.2 | 219.35 | 240.6 | 4.91 | 4.91 | 227.7 | 227.7 | 0.54 | 0.6 | 221.4 | 240.1 | 0 | 0 | 221.4 | 240.5
2026-09-01 | 12:00:00 | 0.9 | 12.8 | 222.43 | 241.5 | 4.91 | 4.91 | 227.7 | 227.7 | 0.54 | 1.08 | 225.9 | 240.8 | 0 | 0 | 227.6 | 238.7
2026-09-01 | 13:00:00 | 1.2 | 21.1 | 217.86 | 241.5 | 4.91 | 4.91 | 227.7 | 227.7 | 0.53 | 1.05 | 221.5 | 239.3 | 0 | 0 | 222.4 | 239.9
2026-09-01 | 14:00:00 | 1.3 | 22.3 | 215.38 | 242.89 | 4.91 | 4.91 | 227.7 | 227.7 | 0.53 | 1.06 | 221.4 | 240.1 | 0 | 0 | 219.7 | 240.5
2026-09-01 | 15:00:00 | 1.1 | 13.6 | 219.55 | 241.6 | 4.91 | 4.91 | 227.7 | 227.7 | 1.03 | 1.18 | 215.9 | 240.9 | 0 | 0 | 216.8 | 241.1
2026-09-01 | 16:00:00 | 2.1 | 3.7 | 209.72 | 239.91 | 4.91 | 4.91 | 227.7 | 227.7 | 0.85 | 1.64 | 209.3 | 235.8 | 0 | 0 | 209.3 | 239.3
2026-09-01 | 17:00:00 | 2.3 | 20.1 | 216.87 | 241.2 | 4.91 | 4.91 | 227.7 | 227.7 | 0.82 | 0.9 | 216.6 | 239.8 | 0 | 0 | 214.6 | 239.3
2026-09-01 | 18:00:00 | 2.1 | 13.2 | 217.86 | 237.23 | 4.91 | 4.91 | 227.7 | 227.7 | 0.85 | 1.19 | 221.6 | 237.2 | 0 | 0 | 221.9 | 237.3
2026-09-01 | 19:00:00 | 1.5 | 14.5 | 223.23 | 241.1 | 4.91 | 4.91 | 227.7 | 227.7 | 0.83 | 1.12 | 223.9 | 239.8 | 0 | 0 | 223.7 | 237.3
2026-09-01 | 20:00:00 | 2 | 14.1 | 226.7 | 240.11 | 4.91 | 4.91 | 227.7 | 227.7 | 0.43 | 1.06 | 230.5 | 239.9 | 0 | 0 | 230.2 | 237.6
2026-09-01 | 21:00:00 | 1.4 | 3 | 233.06 | 242.99 | 4.91 | 4.91 | 227.7 | 227.7 | 0.46 | 0.85 | 232.7 | 242.8 | 0 | 0 | 231.9 | 238.7
2026-09-01 | 22:00:00 | 1.3 | 4.1 | 237.13 | 242.29 | 4.91 | 4.91 | 227.7 | 227.7 | 0.53 | 0.56 | 237 | 241.9 | 0 | 0 | 234.4 | 241.4
2026-09-01 | 23:00:00 | 1.1 | 3.9 | 233.85 | 242.19 | 4.91 | 4.91 | 227.7 | 227.7 | 0.52 | 0.53 | 236.4 | 242.1 | 0 | 0 | 235 | 242
2026-09-02 | 00:00:00 | 1.1 | 4.2 | 234.84 | 243.68 | 4.91 | 4.91 | 227.7 | 227.7 | 0.52 | 0.53 | 237.6 | 243.7 | 0 | 0 | 236.7 | 242
2026-09-02 | 01:00:00 | 1 | 2.5 | 232.86 | 243.38 | 4.91 | 4.91 | 227.7 | 227.7 | 0.51 | 0.54 | 236.5 | 243.1 | 0 | 0 | 233.6 | 241.8
2026-09-02 | 02:00:00 | 1 | 1.9 | 239.71 | 244.18 | 4.91 | 4.91 | 227.7 | 227.7 | 0.29 | 0.54 | 241.1 | 246.3 | 0 | 0 | 237.9 | 243.2
2026-09-02 | 03:00:00 | 1 | 12.8 | 232.76 | 246.96 | 4.91 | 4.91 | 227.7 | 227.7 | 0.28 | 0.3 | 237.9 | 246.3 | 0 | 0 | 232.5 | 244.1
2026-09-02 | 04:00:00 | 1.1 | 12.3 | 227.2 | 242.69 | 4.91 | 4.91 | 227.7 | 227.7 | 0.29 | 0.3 | 229.9 | 242.6 | 0 | 0 | 228.4 | 242
2026-09-02 | 05:00:00 | 1.1 | 13.3 | 227.6 | 244.77 | 4.91 | 4.91 | 227.7 | 227.7 | 0.28 | 1.1 | 226.4 | 244.5 | 0 | 0 | 226.6 | 244.4
2026-09-02 | 06:00:00 | 1.1 | 12.4 | 228.09 | 248.15 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 12.38 | 224.7 | 247.5 | 0 | 0 | 225.9 | 244.4
2026-09-02 | 07:00:00 | 1.3 | 17.1 | 221.04 | 243.38 | 4.91 | 4.91 | 227.7 | 227.7 | 0.3 | 1.38 | 221.8 | 241.3 | 0 | 0 | 220.4 | 239.9
2026-09-02 | 08:00:00 | 1.3 | 12.8 | 228.49 | 252.02 | 4.91 | 4.91 | 227.7 | 227.7 | 0.29 | 6.88 | 229.7 | 250.9 | 0 | 0 | 226.3 | 250
2026-09-02 | 09:00:00 | 1.5 | 18.8 | 223.33 | 246.66 | 4.91 | 4.91 | 227.7 | 227.7 | 0.54 | 6.85 | 228 | 243.5 | 0 | 0 | 227.1 | 247.8
2026-09-02 | 10:00:00 | 1.2 | 18.7 | 222.93 | 243.48 | 4.91 | 4.91 | 227.7 | 227.7 | 0.54 | 1.04 | 221 | 242.6 | 0 | 0 | 219.6 | 240.8
2026-09-02 | 11:00:00 | 1.3 | 9.4 | 226.3 | 246.26 | 4.91 | 4.91 | 227.7 | 227.7 | 0.54 | 4.73 | 225.8 | 244.7 | 0 | 0 | 227.1 | 244.4
2026-09-02 | 12:00:00 | 1.6 | 13.6 | 223.23 | 243.48 | 4.91 | 4.91 | 227.7 | 227.7 | 0.75 | 1.07 | 225.3 | 242.6 | 0 | 0 | 224.4 | 244.3
2026-09-02 | 13:00:00 | 2 | 22 | 216.18 | 241.4 | 4.91 | 4.91 | 227.7 | 227.7 | 0.29 | 1.3 | 221.2 | 239 | 0 | 0 | 219.4 | 239.3
2026-09-02 | 14:00:00 | 1.8 | 11.5 | 221.44 | 242.69 | 4.91 | 4.91 | 227.7 | 227.7 | 0.29 | 1.09 | 221 | 241.3 | 0 | 0 | 223.2 | 241.4
2026-09-02 | 15:00:00 | 1.7 | 18.8 | 209.92 | 241.6 | 4.91 | 4.91 | 227.7 | 227.7 | 0.99 | 7.38 | 209.6 | 240.6 | 0 | 0 | 205.8 | 237.3
2026-09-02 | 16:00:00 | 1.8 | 5.8 | 217.37 | 238.32 | 4.91 | 4.91 | 227.7 | 227.7 | 0.89 | 1.58 | 215 | 233.8 | 0 | 0 | 214.4 | 233.4
2026-09-02 | 17:00:00 | 2 | 13.7 | 209.52 | 236.33 | 4.91 | 4.91 | 227.7 | 227.7 | 0.87 | 1.1 | 213.6 | 233.9 | 0 | 0 | 215.1 | 234.3
2026-09-02 | 18:00:00 | 2 | 11.1 | 219.45 | 238.82 | 4.91 | 4.91 | 227.7 | 227.7 | 0.83 | 1.04 | 220.9 | 236.1 | 0 | 0 | 224.2 | 234.3
2026-09-02 | 19:00:00 | 1.3 | 12.9 | 219.25 | 242.29 | 4.91 | 4.91 | 227.7 | 227.7 | 0.88 | 1.2 | 219.8 | 242.3 | 0 | 0 | 218.2 | 238.7
2026-09-02 | 20:00:00 | 1.7 | 13.8 | 223.82 | 241.3 | 4.91 | 4.91 | 227.7 | 227.7 | 0.54 | 1.33 | 227.2 | 241.4 | 0 | 0 | 227.6 | 238.4
2026-09-02 | 21:00:00 | 1.2 | 4.7 | 222.83 | 243.29 | 4.91 | 4.91 | 227.7 | 227.7 | 0.28 | 0.54 | 224.2 | 243.4 | 0 | 0 | 225.5 | 242
2026-09-02 | 22:00:00 | 1 | 2.1 | 234.25 | 243.38 | 4.91 | 4.91 | 227.7 | 227.7 | 0.28 | 0.3 | 235.5 | 242.7 | 0 | 0 | 235.6 | 241.1
2026-09-02 | 23:00:00 | 1 | 3.8 | 233.85 | 241.2 | 4.91 | 4.91 | 227.7 | 227.7 | 0.28 | 0.29 | 235.7 | 240.8 | 0 | 0 | 235.8 | 241.1
2026-09-03 | 00:00:00 | 0.9 | 3.8 | 230.48 | 242.29 | 4.91 | 4.91 | 227.7 | 227.7 | 0.28 | 0.67 | 233.7 | 241.6 | 0 | 0 | 233.3 | 241.1
2026-09-03 | 01:00:00 | 1 | 3.9 | 237.43 | 242.19 | 4.91 | 4.91 | 227.7 | 227.7 | 0.52 | 0.56 | 238 | 241.9 | 0 | 0 | 235 | 241.1
2026-09-03 | 02:00:00 | 1 | 4.2 | 237.03 | 244.68 | 4.91 | 4.91 | 227.7 | 227.7 | 0.51 | 0.53 | 237.8 | 244.2 | 0 | 0 | 239.3 | 241.4
2026-09-03 | 03:00:00 | 0.8 | 3 | 237.43 | 243.29 | 4.91 | 4.91 | 227.7 | 227.7 | 0.51 | 0.53 | 236.2 | 243.1 | 0 | 0 | 238.7 | 241.4
2026-09-03 | 04:00:00 | 0.9 | 13 | 232.56 | 244.68 | 4.91 | 4.91 | 227.7 | 227.7 | 0.28 | 0.52 | 235.2 | 244.1 | 0 | 0 | 233 | 244.3
2026-09-03 | 05:00:00 | 1 | 12.7 | 233.36 | 247.95 | 4.91 | 4.91 | 227.7 | 227.7 | 0.28 | 12.4 | 232.3 | 248 | 0 | 0 | 231.7 | 244.7
2026-09-03 | 06:00:00 | 0.9 | 12.7 | 228.19 | 244.38 | 4.91 | 4.91 | 227.7 | 227.7 | 0.29 | 0.84 | 229 | 243.8 | 0 | 0 | 228.4 | 242
2026-09-03 | 07:00:00 | 1.1 | 13 | 222.43 | 243.58 | 4.91 | 4.91 | 227.7 | 227.7 | 0.34 | 10.75 | 223.2 | 243.8 | 0 | 0 | 221.9 | 243.2
2026-09-03 | 08:00:00 | 6.1 | 18 | 211.81 | 239.21 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 5.53 | 212.7 | 239.7 | 0 | 0 | 210 | 239.9
2026-09-03 | 09:00:00 | 0.9 | 12.2 | 224.52 | 246.66 | 4.91 | 4.91 | 227.7 | 227.7 | 0.29 | 0.57 | 227.6 | 244.1 | 0 | 0 | 226.6 | 245
2026-09-03 | 10:00:00 | 1 | 13.3 | 209.52 | 238.82 | 4.91 | 4.91 | 227.7 | 227.7 | 0.28 | 0.35 | 209.8 | 237.9 | 0 | 0 | 209.1 | 235.6
2026-09-03 | 11:00:00 | 1 | 11.9 | 214.19 | 240.31 | 4.91 | 4.91 | 227.7 | 227.7 | 0.29 | 6.57 | 216 | 238.7 | 0 | 0 | 216.5 | 239.3
2026-09-03 | 12:00:00 | 0.9 | 22.2 | 217.37 | 243.78 | 4.91 | 4.91 | 227.7 | 227.7 | 0.54 | 0.59 | 221.6 | 242.3 | 0 | 0 | 223.9 | 239.9
2026-09-03 | 13:00:00 | 1.4 | 16.1 | 219.06 | 245.47 | 4.91 | 4.91 | 227.7 | 227.7 | 0.55 | 1.11 | 221.7 | 244.6 | 0 | 0 | 222.2 | 242.3
2026-09-03 | 14:00:00 | 1.1 | 2 | 231.07 | 243.29 | 4.91 | 4.91 | 227.7 | 227.7 | 0.79 | 1.13 | 230.1 | 241 | 0 | 0 | 230 | 242.3
2026-09-03 | 15:00:00 | 1.3 | 13.4 | 205.05 | 239.91 | 4.91 | 4.91 | 227.7 | 227.7 | 0.69 | 6.95 | 198.1 | 238.6 | 0 | 0 | 195.5 | 237.6
2026-09-03 | 16:00:00 | 1.3 | 12.5 | 209.72 | 238.02 | 4.91 | 4.91 | 227.7 | 227.7 | 0.63 | 1.33 | 203.5 | 234.4 | 0 | 0 | 201.6 | 235
2026-09-03 | 17:00:00 | 2 | 17.4 | 201.68 | 234.55 | 4.91 | 4.91 | 227.7 | 227.7 | 0.97 | 1.26 | 199.5 | 232.4 | 0 | 0 | 201.4 | 232.5
2026-09-03 | 18:00:00 | 1.9 | 5.2 | 213.89 | 236.14 | 4.91 | 4.91 | 227.7 | 227.7 | 0.89 | 1.46 | 211.6 | 234.4 | 0 | 0 | 209.8 | 233.6
2026-09-03 | 19:00:00 | 2 | 14 | 219.35 | 239.21 | 4.91 | 4.91 | 227.7 | 227.7 | 0.86 | 1.87 | 224.9 | 238.7 | 0 | 0 | 224.9 | 237
2026-09-03 | 20:00:00 | 2.4 | 4.1 | 230.08 | 244.97 | 4.91 | 4.91 | 227.7 | 227.7 | 0.63 | 1.43 | 230.8 | 244.9 | 0 | 0 | 229.3 | 242
2026-09-03 | 21:00:00 | 2.1 | 5 | 226.4 | 240.01 | 4.91 | 4.91 | 227.7 | 227.7 | 0.51 | 0.63 | 227.1 | 240.2 | 0 | 0 | 233 | 239.9
2026-09-03 | 22:00:00 | 1 | 4.8 | 230.28 | 242.09 | 4.91 | 4.91 | 227.7 | 227.7 | 0.5 | 0.52 | 234.9 | 241.8 | 0 | 0 | 233.6 | 239.8
2026-09-03 | 23:00:00 | 1.1 | 2.2 | 231.67 | 242.99 | 4.91 | 4.91 | 227.7 | 227.7 | 0.28 | 0.52 | 234.7 | 242.4 | 0 | 0 | 233.4 | 240.5
2026-09-04 | 00:00:00 | 1.1 | 1.6 | 232.76 | 242.79 | 4.91 | 4.91 | 227.7 | 227.7 | 0.28 | 0.29 | 235.4 | 241.9 | 0 | 0 | 236.7 | 241.1
2026-09-04 | 01:00:00 | 0.9 | 3.7 | 238.42 | 242.49 | 4.91 | 4.91 | 227.7 | 227.7 | 0.28 | 0.29 | 239.2 | 242.6 | 0 | 0 | 240.5 | 241.1
2026-09-04 | 02:00:00 | 0.9 | 3.6 | 237.72 | 242.59 | 4.91 | 4.91 | 227.7 | 227.7 | 0.28 | 0.66 | 239.5 | 242.6 | 0 | 0 | 239.9 | 240.8
2026-09-04 | 03:00:00 | 0.9 | 4 | 237.72 | 242.89 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 240.2 | 241.4 | 0 | 0 | 238.4 | 240.9
2026-09-04 | 04:00:00 | 0.9 | 1.5 | 233.26 | 244.77 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 234.5 | 241 | 0 | 0 | 233.3 | 244.3
2026-09-04 | 05:00:00 | 0.9 | 13.1 | 228.79 | 246.56 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 236 | 236 | 0 | 0 | 230.6 | 245.3
2026-09-04 | 06:00:00 | 0.9 | 12.8 | 218.36 | 241.7 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 236 | 236 | 0 | 0 | 218.5 | 239.3
2026-09-04 | 07:00:00 | 1.1 | 20.1 | 213.2 | 241.3 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 236 | 238.9 | 0 | 0 | 214.2 | 239.3
2026-09-04 | 08:00:00 | 1.3 | 20.1 | 206.05 | 239.41 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 238.9 | 0 | 0 | 209 | 236.4
2026-09-04 | 09:00:00 | 1.1 | 13 | 216.37 | 241.3 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 216.1 | 240.2
2026-09-04 | 10:00:00 | 1.4 | 9 | 213 | 244.18 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 217 | 239.9
2026-09-04 | 11:00:00 | 1.3 | 21.8 | 213.3 | 245.07 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 219.2 | 244.4
2026-09-04 | 12:00:00 | 1.1 | 13 | 212.7 | 239.91 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 213.2 | 238.2
2026-09-04 | 13:00:00 | 1.1 | 12.5 | 220.94 | 241.99 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 221.4 | 238.7
2026-09-04 | 14:00:00 | 1.1 | 20.1 | 210.62 | 240.31 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 215.3 | 240.5
2026-09-04 | 15:00:00 | 1.5 | 4.2 | 220.55 | 239.41 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 221.6 | 236.8
2026-09-04 | 16:00:00 | 2 | 14.1 | 218.66 | 248.05 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 221.7 | 248.1
2026-09-04 | 17:00:00 | 2 | 8.7 | 217.17 | 242.89 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 219 | 239.3
2026-09-04 | 18:00:00 | 1.8 | 13.7 | 214.98 | 241.1 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 220.9 | 240.2
2026-09-04 | 19:00:00 | 1.6 | 15.5 | 221.04 | 241.5 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 218.5 | 238.2
2026-09-04 | 20:00:00 | 1.4 | 4 | 220.94 | 236.83 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 213.2 | 235.6
2026-09-04 | 21:00:00 | 1.2 | 2.9 | 235.44 | 241.2 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 235.6 | 240.7
2026-09-04 | 22:00:00 | 1 | 1.7 | 236.73 | 242.29 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 233.9 | 239.3
2026-09-04 | 23:00:00 | 1 | 1.7 | 236.53 | 241.5 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 238.2 | 239.3
2026-09-05 | 00:00:00 | 0.9 | 2.8 | 235.64 | 240.5 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 237 | 238.2
2026-09-05 | 01:00:00 | 0.8 | 4 | 235.34 | 240.5 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 236.4 | 238.2
2026-09-05 | 02:00:00 | 0.8 | 3.8 | 235.04 | 241.2 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 232.5 | 238.7
2026-09-05 | 03:00:00 | 0.9 | 2.5 | 236.23 | 240.31 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 232.5 | 235.9
2026-09-05 | 04:00:00 | 0.9 | 2.1 | 232.16 | 240.5 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 229.2 | 237
2026-09-05 | 05:00:00 | 0.8 | 12.4 | 224.22 | 241.4 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 224.9 | 237
2026-09-05 | 06:00:00 | 0.8 | 12 | 218.86 | 241.7 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 220.5 | 240.2
2026-09-05 | 07:00:00 | 0.9 | 19 | 217.86 | 256.48 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 218.2 | 256.5
2026-09-05 | 08:00:00 | 1 | 13.3 | 216.08 | 245.37 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 215.1 | 245.3
2026-09-05 | 09:00:00 | 1.1 | 20.5 | 208.93 | 243.88 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.56 | 237.4 | 237.4 | 0 | 0 | 211.6 | 240.4
2026-09-05 | 10:00:00 | 0.9 | 3.2 | 227.69 | 243.58 | 4.91 | 4.91 | 227.7 | 227.7 | 0.56 | 0.58 | 237.4 | 237.4 | 0 | 0 | 227.6 | 244.4
2026-09-05 | 11:00:00 | 1.1 | 23.2 | 215.68 | 241.99 | 4.91 | 4.91 | 227.7 | 227.7 | 0.58 | 0.58 | 230.6 | 237.4 | 0 | 0 | 217.3 | 241.1
2026-09-05 | 12:00:00 | 2.4 | 41.8 | 205.15 | 240.6 | 4.91 | 10.11 | 225.6 | 227.7 | 0.58 | 0.58 | 232.5 | 232.9 | 0 | 0 | 214.6 | 238.2
2026-09-05 | 13:00:00 | 1.9 | 28.5 | 216.77 | 242.09 | 10.11 | 10.11 | 225.6 | 225.6 | 0.58 | 0.58 | 232.5 | 232.5 | 0 | 0 | 221.4 | 240.8
2026-09-05 | 14:00:00 | 1.7 | 13.4 | 222.93 | 241.3 | 10.11 | 10.11 | 225.6 | 225.6 | 0.58 | 0.58 | 232.5 | 232.5 | 0 | 0 | 223.7 | 240.5
2026-09-05 | 15:00:00 | 1.1 | 12.8 | 211.71 | 238.42 | 10.11 | 10.11 | 225.6 | 225.6 | 0.58 | 0.58 | 232.5 | 232.5 | 0 | 0 | 211.2 | 237.3
2026-09-05 | 16:00:00 | 1.6 | 18.3 | 211.21 | 236.53 | 10.11 | 10.11 | 225.6 | 225.6 | 0.58 | 0.58 | 232.5 | 232.5 | 0 | 0 | 215.1 | 236.1
2026-09-05 | 17:00:00 | 1.8 | 9.4 | 214.59 | 237.72 | 10.11 | 10.11 | 225.6 | 225.6 | 0.58 | 0.58 | 232.5 | 232.5 | 0 | 0 | 215.3 | 236.1
2026-09-05 | 18:00:00 | 1.6 | 13.3 | 222.73 | 243.88 | 10.11 | 10.11 | 225.6 | 225.6 | 0.58 | 0.58 | 232.5 | 232.5 | 0 | 0 | 223.5 | 241.4
2026-09-05 | 19:00:00 | 1.9 | 13.7 | 225.61 | 243.09 | 2.79 | 14.55 | 216 | 239.8 | 0.58 | 12.66 | 231.4 | 240 | 0 | 0 | 226.3 | 241.4
2026-09-05 | 20:00:00 | 1.4 | 5.2 | 231.17 | 244.08 | 2.57 | 13.98 | 233.4 | 241.1 | 0.87 | 1.03 | 231 | 242.3 | 0 | 0 | 229.9 | 242
2026-09-05 | 21:00:00 | 1.2 | 1.9 | 236.43 | 241.99 | 2.58 | 3.02 | 240.8 | 240.8 | 1.03 | 1.03 | 242 | 242 | 0 | 0 | 235.6 | 241.4
2026-09-05 | 22:00:00 | 1 | 4 | 232.36 | 242.29 | 3.02 | 3.02 | 240.8 | 240.8 | 1.03 | 1.03 | 242 | 242 | 0 | 0 | 234.4 | 241.4
2026-09-05 | 23:00:00 | 0.9 | 1.7 | 230.87 | 239.91 | 3.02 | 3.02 | 240.8 | 240.8 | 1.03 | 1.03 | 242 | 242 | 0 | 0 | 235 | 240.2
2026-09-06 | 00:00:00 | 0.9 | 4.4 | 234.45 | 241.2 | 3.02 | 3.02 | 240.8 | 240.8 | 1.03 | 1.03 | 242 | 242 | 0 | 0 | 237.3 | 239.6
2026-09-06 | 01:00:00 | 0.8 | 1.5 | 236.63 | 240.8 | 3.02 | 3.02 | 240.8 | 240.8 | 1.03 | 1.03 | 242 | 242 | 0 | 0 | 233.9 | 239.6
2026-09-06 | 02:00:00 | 0.8 | 3.7 | 236.83 | 242.79 | 3.02 | 3.02 | 240.8 | 241.8 | 1.03 | 1.03 | 242 | 242 | 0 | 0 | 239.3 | 240.2
2026-09-06 | 03:00:00 | 0.8 | 2.5 | 231.17 | 241.6 | 3.02 | 3.02 | 241.8 | 241.8 | 1.03 | 1.03 | 242 | 242 | 0 | 0 | 235 | 240.8
2026-09-06 | 04:00:00 | 0.9 | 12.6 | 219.95 | 241.5 | 3.02 | 3.02 | 241.8 | 241.8 | 1.03 | 1.03 | 242 | 242 | 0 | 0 | 229.5 | 238.7
2026-09-06 | 05:00:00 | 1 | 12.4 | 227.1 | 240.21 | 3.02 | 3.02 | 241.8 | 241.8 | 1.03 | 1.03 | 242 | 242 | 0 | 0 | 223.5 | 238.2
2026-09-06 | 06:00:00 | 0.9 | 13.1 | 220.45 | 240.21 | 3.02 | 3.02 | 241.8 | 241.8 | 1.03 | 1.03 | 242 | 242 | 0 | 0 | 224.5 | 237
2026-09-06 | 07:00:00 | 0.9 | 13.1 | 220.55 | 243.09 | 3.02 | 3.02 | 241.8 | 241.8 | 1.03 | 1.03 | 242 | 242 | 0 | 0 | 218.5 | 244.4
2026-09-06 | 08:00:00 | 1 | 12.4 | 213 | 238.82 | 3.02 | 3.02 | 241.8 | 241.8 | 1.03 | 1.03 | 242 | 242 | 0 | 0 | 215.5 | 237.4
2026-09-06 | 09:00:00 | 1.2 | 20.2 | 207.83 | 242.39 | 3.02 | 3.02 | 241.8 | 241.8 | 1.03 | 1.03 | 242 | 242 | 0 | 0 | 210 | 242.6
2026-09-06 | 10:00:00 | 1.2 | 12 | 212.9 | 246.36 | 3.02 | 3.02 | 241.8 | 241.8 | 1.03 | 1.03 | 242 | 242 | 0 | 0 | 217.7 | 243.2
2026-09-06 | 11:00:00 | 1.6 | 24.3 | 208.73 | 239.71 | 1.56 | 10.57 | 210.2 | 242 | 0.56 | 1.09 | 241.3 | 242 | 0 | 0 | 211.8 | 239.6
2026-09-06 | 12:00:00 | 1.5 | 22.6 | 201.38 | 239.11 | 2.45 | 15.71 | 217.8 | 237.4 | 0.53 | 1.09 | 226.3 | 241.8 | 0 | 0 | 205.2 | 239.9
2026-09-06 | 13:00:00 | 1.8 | 9.5 | 222.83 | 240.8 | 2.62 | 9.34 | 222.7 | 238.7 | 0.3 | 0.53 | 224.5 | 236 | 0 | 0 | 219.7 | 239.3
2026-09-06 | 14:00:00 | 1.8 | 13.1 | 229.28 | 244.97 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 230.3 | 230.5 | 0 | 0 | 227.6 | 245.6
2026-09-06 | 15:00:00 | 1.7 | 9.3 | 222.23 | 236.93 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 230.5 | 230.5 | 0 | 0 | 223.5 | 237.3
2026-09-06 | 16:00:00 | 1.6 | 21.3 | 201.28 | 230.67 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 230.5 | 230.5 | 0 | 0 | 199.1 | 229
2026-09-06 | 17:00:00 | 1.9 | 21.2 | 198.4 | 234.84 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 230.5 | 230.5 | 0 | 0 | 203.7 | 234.7
2026-09-06 | 18:00:00 | 1.7 | 13.2 | 213.2 | 238.52 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 230.5 | 230.5 | 0 | 0 | 217 | 239.3
2026-09-06 | 19:00:00 | 2.1 | 14.3 | 218.36 | 235.34 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 230.5 | 230.5 | 0 | 0 | 218.7 | 233.6
2026-09-06 | 20:00:00 | 1.6 | 14.1 | 223.82 | 237.23 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 230.5 | 230.5 | 0 | 0 | 224.7 | 235.6
2026-09-06 | 21:00:00 | 1.3 | 3.8 | 234.84 | 243.19 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 230.5 | 230.5 | 0 | 0 | 235.6 | 241.1
2026-09-06 | 22:00:00 | 1.3 | 4.1 | 231.47 | 242.49 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 230.5 | 230.5 | 0 | 0 | 234.2 | 240.5
2026-09-06 | 23:00:00 | 1 | 2.5 | 230.28 | 241.5 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 230.5 | 230.5 | 0 | 0 | 234.2 | 240.8
2026-09-07 | 00:00:00 | 1 | 2.8 | 233.65 | 241.7 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 230.5 | 233.9 | 0 | 0 | 233 | 240.5
2026-09-07 | 01:00:00 | 0.9 | 1.6 | 233.65 | 243.09 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 231.9 | 239.3
2026-09-07 | 02:00:00 | 1 | 4 | 231.96 | 240.21 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 237.3 | 239
2026-09-07 | 03:00:00 | 0.9 | 4.3 | 236.83 | 242.99 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 233.6 | 239.9
2026-09-07 | 04:00:00 | 0.9 | 2.7 | 227.99 | 242.49 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 231.4 | 242.6
2026-09-07 | 05:00:00 | 0.9 | 3.7 | 222.63 | 247.85 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 214.9 | 245.3
2026-09-07 | 06:00:00 | 1.1 | 12.9 | 215.38 | 239.31 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 215.4 | 238.7
2026-09-07 | 07:00:00 | 1.2 | 13.7 | 219.65 | 246.66 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 219.4 | 242
2026-09-07 | 08:00:00 | 1.1 | 14.3 | 214.09 | 246.46 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 213.8 | 245.9
2026-09-07 | 09:00:00 | 0.9 | 11.9 | 219.65 | 241.8 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 224.2 | 239.3
2026-09-07 | 10:00:00 | 1 | 12.8 | 229.68 | 247.16 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 230.6 | 242.6
2026-09-07 | 11:00:00 | 0.9 | 13 | 225.91 | 248.95 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 225 | 247.2
2026-09-07 | 12:00:00 | 1.1 | 14.6 | 218.36 | 241.4 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 219 | 238.7
2026-09-07 | 13:00:00 | 2 | 23.3 | 210.32 | 240.31 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 213.8 | 238.3
2026-09-07 | 14:00:00 | 1.3 | 13.1 | 227.69 | 240.6 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 227.6 | 239.3
2026-09-07 | 15:00:00 | 1.3 | 16.4 | 213.4 | 239.81 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 216.4 | 239.3
2026-09-07 | 16:00:00 | 1.4 | 13.5 | 202.47 | 245.07 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 208.3 | 242.6
2026-09-07 | 17:00:00 | 2.3 | 14 | 209.62 | 240.5 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 211.1 | 238.7
2026-09-07 | 18:00:00 | 1.8 | 10.7 | 222.13 | 242.89 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.4 | 241.4
2026-09-07 | 19:00:00 | 1.8 | 14.3 | 220.25 | 241 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 222.6 | 239.9
2026-09-07 | 20:00:00 | 1.3 | 4 | 226.5 | 241.5 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 230 | 238.7
2026-09-07 | 21:00:00 | 1.1 | 3.3 | 230.87 | 238.42 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 230.8 | 236.1
2026-09-07 | 22:00:00 | 1.1 | 4.1 | 229.88 | 238.72 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 230.3 | 236.1
2026-09-07 | 23:00:00 | 1 | 1.6 | 228.39 | 236.83 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 227.4 | 233.4
2026-09-08 | 00:00:00 | 1.2 | 1.9 | 233.06 | 241.8 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 233.4 | 241.4
2026-09-08 | 01:00:00 | 0.9 | 3.5 | 237.03 | 241.6 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 235.6 | 241.4
2026-09-08 | 02:00:00 | 0.9 | 13.1 | 231.37 | 242.29 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 236.1 | 241.7
2026-09-08 | 03:00:00 | 0.9 | 2.2 | 237.43 | 243.68 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 235 | 241.7
2026-09-08 | 04:00:00 | 0.8 | 2.7 | 229.38 | 245.67 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 230.8 | 244.7
2026-09-08 | 05:00:00 | 0.9 | 12.2 | 226.4 | 247.46 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 224.2 | 245.6
2026-09-08 | 06:00:00 | 0.9 | 12.4 | 225.31 | 240.9 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 228.4 | 240.8
2026-09-08 | 07:00:00 | 0.9 | 12.8 | 221.64 | 246.46 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 228.4 | 242
2026-09-08 | 08:00:00 | 1.1 | 12.2 | 219.35 | 240.31 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 219 | 237.6
2026-09-08 | 09:00:00 | 1.1 | 26.3 | 203.27 | 241 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 212.3 | 240.2
2026-09-08 | 10:00:00 | 1.1 | 10.9 | 206.44 | 235.14 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 209.3 | 234.5
2026-09-08 | 11:00:00 | 1.1 | 3.8 | 214.98 | 236.83 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 217 | 237.6
2026-09-08 | 12:00:00 | 1.2 | 13.3 | 220.64 | 241.4 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.2 | 239.9
2026-09-08 | 13:00:00 | 1.1 | 12.4 | 221.74 | 242.69 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 223 | 242
2026-09-08 | 14:00:00 | 1.5 | 32.3 | 211.71 | 241.5 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 220.4 | 241.7
2026-09-08 | 15:00:00 | 1.7 | 23.2 | 213.99 | 240.11 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 210.2 | 240.2
2026-09-08 | 16:00:00 | 2.5 | 23.4 | 209.62 | 239.31 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 213 | 238.2
2026-09-08 | 17:00:00 | 2 | 8.8 | 219.16 | 240.21 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.2 | 239.8
2026-09-08 | 18:00:00 | 1.8 | 13.7 | 216.08 | 239.61 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 222.7 | 239.3
2026-09-08 | 19:00:00 | 1.6 | 14.3 | 223.92 | 241.1 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 222.7 | 237.6
2026-09-08 | 20:00:00 | 1.7 | 3.2 | 228.59 | 241.99 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 227.4 | 240.8
2026-09-08 | 21:00:00 | 1.2 | 4.7 | 233.26 | 240.21 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 233 | 239.3
2026-09-08 | 22:00:00 | 1 | 1.8 | 236.53 | 243.78 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 237 | 242.6
2026-09-08 | 23:00:00 | 1 | 3.8 | 235.94 | 241.7 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 237 | 240.2
2026-09-09 | 00:00:00 | 0.9 | 2.2 | 233.85 | 242.29 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 233.3 | 241.1
2026-09-09 | 01:00:00 | 0.8 | 4.1 | 232.06 | 243.68 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 235 | 241.4
2026-09-09 | 02:00:00 | 0.8 | 1.8 | 238.42 | 241.8 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 239.6 | 240.8
2026-09-09 | 03:00:00 | 0.8 | 3.9 | 234.55 | 244.18 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 239.6 | 240.2
2026-09-09 | 04:00:00 | 0.9 | 1.7 | 228.59 | 244.18 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 229.8 | 243.5
2026-09-09 | 05:00:00 | 0.9 | 12.5 | 224.02 | 247.95 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 222.4 | 245.9
2026-09-09 | 06:00:00 | 1 | 12.7 | 214.79 | 244.68 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 214.9 | 244.7
2026-09-09 | 07:00:00 | 0.9 | 13.1 | 218.76 | 245.57 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 215.3 | 244.7
2026-09-09 | 08:00:00 | 1.3 | 12.3 | 222.73 | 244.48 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 227.1 | 243.2
2026-09-09 | 09:00:00 | 1.3 | 17.4 | 209.62 | 243.19 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 216.4 | 238.7
2026-09-09 | 10:00:00 | 1.3 | 12.7 | 227.3 | 242.69 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.2 | 243
2026-09-09 | 11:00:00 | 1.5 | 13.2 | 213.79 | 237.92 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 219 | 236.9
2026-09-09 | 12:00:00 | 1.8 | 13.2 | 224.52 | 242.69 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 224.4 | 238.7
2026-09-09 | 13:00:00 | 1.6 | 2.7 | 224.72 | 243.19 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 227.5 | 242.6
2026-09-09 | 14:00:00 | 1.7 | 11.2 | 223.62 | 248.85 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 225.5 | 248.8
2026-09-09 | 15:00:00 | 1.6 | 24 | 218.26 | 240.31 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 223.7 | 239.5
2026-09-09 | 16:00:00 | 1.7 | 13.5 | 210.22 | 238.42 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 210.5 | 235
2026-09-09 | 17:00:00 | 1.6 | 18.2 | 209.92 | 239.21 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.2 | 234.4
2026-09-09 | 18:00:00 | 1.9 | 13.3 | 219.06 | 240.8 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 219 | 237.6
2026-09-09 | 19:00:00 | 1.9 | 14.8 | 221.44 | 244.18 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 226.1 | 244.7
2026-09-09 | 20:00:00 | 1.7 | 13.9 | 221.34 | 242.89 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 222.2 | 239.6
2026-09-09 | 21:00:00 | 1.2 | 2.8 | 234.55 | 244.08 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 233.3 | 240.8
2026-09-09 | 22:00:00 | 1 | 2.6 | 235.14 | 242.49 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 238.2 | 240.8
2026-09-09 | 23:00:00 | 0.9 | 1.8 | 232.86 | 243.19 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 238.2 | 240.8
2026-09-10 | 00:00:00 | 0.9 | 1.7 | 231.17 | 241.3
2026-09-10 | 01:00:00 | 0.9 | 3.6 | 237.03 | 242.59 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 240.2 | 240.8
2026-09-10 | 02:00:00 | 0.8 | 2.8 | 236.53 | 243.68 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 235.9 | 242
2026-09-10 | 03:00:00 | 0.8 | 1.7 | 238.42 | 243.48 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 236.2 | 242
2026-09-10 | 04:00:00 | 0.8 | 2 | 229.18 | 241.99 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 231.4 | 242
2026-09-10 | 05:00:00 | 0.9 | 12.6 | 228.09 | 246.56 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 229.2 | 245.4
2026-09-10 | 06:00:00 | 0.9 | 12.4 | 220.94 | 240.7 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 219 | 238.7
2026-09-10 | 07:00:00 | 1 | 13.2 | 210.71 | 241.89 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 209.3 | 239.9
2026-09-10 | 08:00:00 | 1 | 12.2 | 218.76 | 245.57 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 219.7 | 245.7
2026-09-10 | 09:00:00 | 1.1 | 12.5 | 221.14 | 245.17 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.7 | 245.7
2026-09-10 | 10:00:00 | 0.9 | 10.3 | 220.84 | 238.92 | 2.78 | 2.78 | 231.4 | 231.4 |  |  |  |  | 0 | 0 | 218.2 | 238.6
2026-09-10 | 11:00:00 | 0.9 | 1.9 | 221.14 | 239.02 | 2.78 | 2.78 | 231.4 | 231.4 |  |  |  |  | 0 | 0 | 222.7 | 238.2
2026-09-10 | 12:00:00 | 1.1 | 13.1 | 222.83 | 245.07 | 2.78 | 2.78 | 231.4 | 231.4 |  |  |  |  | 0 | 0 | 225.5 | 242.6
2026-09-10 | 13:00:00 | 2.1 | 14.4 | 208.43 | 238.62 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 215.3 | 238.3
2026-09-10 | 14:00:00 | 1.8 | 12.7 | 225.91 | 240.7 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 225.3 | 238.7
2026-09-10 | 15:00:00 | 2.1 | 24.2 | 208.63 | 238.72 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 201.2 | 238.7
2026-09-10 | 16:00:00 | 2.2 | 22.9 | 199.89 | 233.06 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 201.8 | 231.4
2026-09-10 | 17:00:00 | 2.5 | 25.4 | 209.52 | 241 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 214.2 | 231.4
2026-09-10 | 18:00:00 | 1.8 | 18.1 | 213.2 | 238.32 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 216.5 | 238.2
2026-09-10 | 19:00:00 | 1.4 | 12.5 | 216.37 | 242.89 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 218.4 | 240.2
2026-09-10 | 20:00:00 | 1.2 | 5 | 227.1 | 242.89 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 229.4 | 239.7
2026-09-10 | 21:00:00 | 1.5 | 2.8 | 234.75 | 241 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 238.2 | 239.3
2026-09-10 | 22:00:00 | 1 | 1.9 | 236.73 | 241.8 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 238.2 | 239.3
2026-09-10 | 23:00:00 | 1 | 1.5 | 235.94 | 242.69 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 239.3 | 239.6
2026-09-11 | 00:00:00 | 0.9 | 1.6 | 239.71 | 242.89 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 238.2 | 243.5
2026-09-11 | 01:00:00 | 0.9 | 3.8 | 236.43 | 242.49 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 238.2 | 243.5
2026-09-11 | 02:00:00 | 0.8 | 3.7 | 236.14 | 241.6 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 238.2 | 239.3
2026-09-11 | 03:00:00 | 0.8 | 3.7 | 234.25 | 244.28 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 238.2 | 241.4
2026-09-11 | 04:00:00 | 0.8 | 12.9 | 232.66 | 246.66 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 235.2 | 242.6
2026-09-11 | 05:00:00 | 1 | 12.5 | 203.86 | 248.15 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 204.4 | 245.6
2026-09-11 | 06:00:00 | 1.1 | 13.2 | 212.7 | 242.69 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 214.9 | 241.4
2026-09-11 | 07:00:00 | 1.2 | 12.9 | 219.85 | 241.89 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 219.7 | 240.2
2026-09-11 | 08:00:00 | 1.1 | 12.8 | 214.69 | 245.17 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 213.2 | 240.8
2026-09-11 | 09:00:00 | 1.1 | 19.5 | 213.79 | 240.7 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 210.7 | 238.7
2026-09-11 | 10:00:00 | 1.2 | 12.6 | 218.76 | 237.62 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 219.2 | 237.3
2026-09-11 | 11:00:00 | 1.5 | 20.8 | 220.84 | 240.21 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 218.5 | 239.3
2026-09-11 | 12:00:00 | 1.5 | 3.9 | 225.11 | 240.41 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 227.1 | 240.1
2026-09-11 | 13:00:00 | 1.2 | 4.1 | 225.21 | 239.31 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 225.8 | 236.6
2026-09-11 | 14:00:00 | 1.3 | 4.7 | 226.4 | 240.6 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.7 | 241.7
2026-09-11 | 15:00:00 | 1.2 | 14.5 | 220.55 | 241.4 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 222.4 | 239.3
2026-09-11 | 16:00:00 | 1.6 | 14.6 | 222.53 | 242.39 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 225.3 | 240.5
2026-09-11 | 17:00:00 | 1.7 | 21.4 | 215.38 | 241.3 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 222.2 | 242
2026-09-11 | 18:00:00 | 1.2 | 12.8 | 218.36 | 243.68 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 223.2 | 241.9
2026-09-11 | 19:00:00 | 1.5 | 14.4 | 224.82 | 243.78 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 226 | 242
2026-09-11 | 20:00:00 | 1.8 | 9.7 | 228.79 | 241.6 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 231.4 | 240.8
2026-09-11 | 21:00:00 | 1.3 | 3.9 | 232.16 | 245.77 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 233.9 | 244.5
2026-09-11 | 22:00:00 | 1 | 1.8 | 231.27 | 242.09 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 227.6 | 239.6
2026-09-11 | 23:00:00 | 0.9 | 3.3 | 229.78 | 240.31 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 229.2 | 239.6
2026-09-12 | 00:00:00 | 0.9 | 2.6 | 236.93 | 242.39 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 236.8 | 242
2026-09-12 | 01:00:00 | 0.8 | 3.7 | 234.84 | 241.6 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 237.6 | 242
2026-09-12 | 02:00:00 | 0.8 | 3.8 | 236.63 | 243.58 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 236.4 | 242.6
2026-09-12 | 03:00:00 | 0.8 | 1.5 | 234.05 | 244.18 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 229.2 | 243.5
2026-09-12 | 04:00:00 | 0.8 | 2.6 | 230.28 | 242.19 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 230.8 | 241.7
2026-09-12 | 05:00:00 | 0.9 | 12.7 | 224.52 | 242.79 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.2 | 242.6
2026-09-12 | 06:00:00 | 0.9 | 13.8 | 226.21 | 242.99 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 227.9 | 239.9
2026-09-12 | 07:00:00 | 0.9 | 12.4 | 226.01 | 245.47 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 227.1 | 241.1
2026-09-12 | 08:00:00 | 0.9 | 12.5 | 227.99 | 255.4 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 228.4 | 254.9
2026-09-12 | 09:00:00 | 1 | 12.9 | 216.47 | 247.95 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 219.4 | 245.3
2026-09-12 | 10:00:00 | 1.3 | 12.6 | 221.34 | 242.69 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 224.3 | 240.5
2026-09-12 | 11:00:00 | 1.3 | 12.9 | 216.28 | 245.47 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 218.8 | 241.6
2026-09-12 | 12:00:00 | 1.4 | 8.3 | 216.87 | 241.3 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 219.4 | 241.7
2026-09-12 | 13:00:00 | 1.7 | 29.1 | 211.51 | 239.61 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 217.5 | 238.2
2026-09-12 | 14:00:00 | 2 | 13.8 | 206.44 | 238.62 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 213.5 | 238.7
2026-09-12 | 15:00:00 | 2 | 4.8 | 215.78 | 242.69 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 216.3 | 242
2026-09-12 | 16:00:00 | 1.8 | 8.4 | 217.07 | 241.2 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 214.8 | 239.9
2026-09-12 | 17:00:00 | 2.3 | 14.1 | 217.76 | 242.79 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.2 | 240.8
2026-09-12 | 18:00:00 | 2.6 | 14.1 | 227.4 | 243.58 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 229.2 | 239.3
2026-09-12 | 19:00:00 | 1.9 | 24.7 | 220.05 | 239.11 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 225.8 | 239.8
2026-09-12 | 20:00:00 | 2 | 2.9 | 227.4 | 238.92 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 227.4 | 238.2
2026-09-12 | 21:00:00 | 1.9 | 3.7 | 233.75 | 239.41 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 233.9 | 240.5
2026-09-12 | 22:00:00 | 1.2 | 3.1 | 229.58 | 242.49 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 231.9 | 238.2
2026-09-12 | 23:00:00 | 1.2 | 3.6 | 235.14 | 240.31 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 237.5 | 237.7
2026-09-13 | 00:00:00 | 1.1 | 3.8 | 234.75 | 240.5 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 235.6 | 238.2
2026-09-13 | 01:00:00 | 0.8 | 2.6 | 237.03 | 241.5 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 233.3 | 240.2
2026-09-13 | 02:00:00 | 1 | 3.9 | 232.76 | 240.6 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 231.9 | 238.7
2026-09-13 | 03:00:00 | 1 | 3.5 | 236.33 | 241.5 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 234.4 | 239.9
2026-09-13 | 04:00:00 | 0.8 | 1.6 | 234.94 | 240.21 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 234.2 | 239.9
2026-09-13 | 05:00:00 | 1.1 | 12.4 | 229.18 | 241.3 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 231.4 | 239.7
2026-09-13 | 06:00:00 | 1.1 | 12.6 | 223.52 | 242.09 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 222.2 | 238.7
2026-09-13 | 07:00:00 | 1.2 | 32.8 | 206.44 | 242.29 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 217.7 | 242
2026-09-13 | 08:00:00 | 1.4 | 23.3 | 223.72 | 248.35 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 224.3 | 245
2026-09-13 | 09:00:00 | 1.5 | 23.1 | 213.2 | 251.43 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 218.9 | 252.6
2026-09-13 | 10:00:00 | 1.4 | 24.1 | 207.44 | 242.09 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 209.8 | 241.4
2026-09-13 | 11:00:00 | 1.3 | 15.2 | 206.54 | 242.59 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 212.4 | 241.4
2026-09-13 | 12:00:00 | 1.3 | 13.2 | 213 | 247.46 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 211.6 | 244.5
2026-09-13 | 13:00:00 | 2.2 | 21.1 | 215.18 | 242.89 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 214.9 | 240.8
2026-09-13 | 14:00:00 | 2.2 | 14.2 | 219.25 | 241.1 | 2.78 | 2.78 | 231.4 | 231.4 |  |  |  |  | 0 | 0 | 214.6 | 238.7
2026-09-13 | 15:00:00 | 1.9 | 13.4 | 214.29 | 243.38 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 215.1 | 243.8
2026-09-13 | 16:00:00 | 1.5 | 4.6 | 211.41 | 242.79 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 210.7 | 240.8
2026-09-13 | 17:00:00 | 2.2 | 21.2 | 206.64 | 241.6 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 211.4 | 239.8
2026-09-13 | 18:00:00 | 2 | 20.9 | 217.47 | 242.49 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 222.4 | 238.7
2026-09-13 | 19:00:00 | 1.7 | 4 | 218.66 | 240.7 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.2 | 237.3
2026-09-13 | 20:00:00 | 1.7 | 13.8 | 227.6 | 243.09 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 230.3 | 241.4
2026-09-13 | 21:00:00 | 1.3 | 3.7 | 233.36 | 240.5 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 237 | 238.7
2026-09-13 | 22:00:00 | 1.1 | 4.1 | 228.59 | 239.71 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 231.4 | 238.2
2026-09-13 | 23:00:00 | 1.1 | 4.8 | 228.19 | 238.32 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 230.8 | 237.3
2026-09-14 | 00:00:00 | 0.9 | 4.2 | 233.45 | 240.5 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 230.8 | 241.4
2026-09-14 | 01:00:00 | 0.9 | 3.1 | 236.23 | 241 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 236.7 | 239.9
2026-09-14 | 02:00:00 | 0.8 | 3.6 | 237.43 | 241.8 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 236.7 | 239.9
2026-09-14 | 03:00:00 | 0.8 | 4.1 | 236.73 | 242.69 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 233.8 | 239.3
2026-09-14 | 04:00:00 | 0.8 | 3.9 | 231.37 | 243.48 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 230 | 241.4
2026-09-14 | 05:00:00 | 1.2 | 12.8 | 224.22 | 241.1 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 227.1 | 239.9
2026-09-14 | 06:00:00 | 1 | 12.2 | 220.94 | 244.28 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 224.5 | 242.1
2026-09-14 | 07:00:00 | 1.1 | 23.5 | 210.81 | 250.83 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 219.4 | 247.2
2026-09-14 | 08:00:00 | 1 | 12.2 | 217.86 | 242.29 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 214.9 | 240.8
2026-09-14 | 09:00:00 | 1 | 12.7 | 222.43 | 243.78 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 222.2 | 245.3
2026-09-14 | 10:00:00 | 0.9 | 11.7 | 223.23 | 244.87 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 224.5 | 243.6
2026-09-14 | 11:00:00 | 1 | 3.9 | 217.57 | 240.8 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.4 | 241.7
2026-09-14 | 12:00:00 | 0.9 | 12.2 | 222.03 | 247.06 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 224.7 | 246.6
2026-09-14 | 13:00:00 | 1.2 | 13.6 | 219.75 | 240.9 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 224.2 | 237.6
2026-09-14 | 14:00:00 | 1.7 | 23.3 | 213.59 | 240.41 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 219.9 | 239.3
2026-09-14 | 15:00:00 | 1.8 | 3.8 | 221.54 | 240.5 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.4 | 240.5
2026-09-14 | 16:00:00 | 1.7 | 17.8 | 213.5 | 235.54 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 208.7 | 235
2026-09-14 | 17:00:00 | 1.4 | 18.7 | 210.62 | 240.31 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 211.2 | 239.3
2026-09-14 | 18:00:00 | 1.7 | 13.4 | 221.14 | 242.49 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 225 | 242.4
2026-09-14 | 19:00:00 | 1.8 | 15.2 | 225.11 | 239.02 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 229 | 236.7
2026-09-14 | 20:00:00 | 2.2 | 3.4 | 232.66 | 240.11 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 236.1 | 236.7
2026-09-14 | 21:00:00 | 1.4 | 4.5 | 230.67 | 240.5 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 230 | 241.1
2026-09-14 | 22:00:00 | 1 | 3.7 | 235.54 | 241.7 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 235.6 | 241.1
2026-09-14 | 23:00:00 | 1 | 2.4 | 235.64 | 245.37 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 235.3 | 245.9
2026-09-15 | 00:00:00 | 1 | 4 | 237.23 | 242.19 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 235 | 240.2
2026-09-15 | 01:00:00 | 0.9 | 3.7 | 236.43 | 241.89 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 240.2 | 241.4
2026-09-15 | 02:00:00 | 1 | 3.9 | 238.92 | 244.48 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 239.3 | 244.7
2026-09-15 | 03:00:00 | 0.9 | 1.8 | 236.23 | 241.4 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 237.7 | 244.7
2026-09-15 | 04:00:00 | 0.9 | 2.8 | 230.28 | 245.57 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 237.7 | 245.9
2026-09-15 | 05:00:00 | 0.9 | 13.1 | 225.71 | 243.19 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 226 | 238.7
2026-09-15 | 06:00:00 | 1 | 14.6 | 225.31 | 244.18 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 225 | 242
2026-09-15 | 07:00:00 | 1.1 | 25.5 | 215.08 | 243.88 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.2 | 242.5
2026-09-15 | 08:00:00 | 1.3 | 20.9 | 213.4 | 246.66 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 214.3 | 246.6
2026-09-15 | 09:00:00 | 1.3 | 13.7 | 216.77 | 244.48 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.8 | 244.7
2026-09-15 | 10:00:00 | 1 | 21.3 | 219.45 | 243.78 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.7 | 240.8
2026-09-15 | 11:00:00 | 1.2 | 21.3 | 226.5 | 250.14 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 229 | 247.2
2026-09-15 | 12:00:00 | 5.8 | 21.5 | 213.2 | 242.99 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 214.2 | 243.5
2026-09-15 | 13:00:00 | 1.3 | 18.4 | 225.21 | 238.02 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.2 | 236.1
2026-09-15 | 14:00:00 | 0.9 | 18 | 220.45 | 242.59 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 222.4 | 238.7
2026-09-15 | 15:00:00 | 1.2 | 3.9 | 216.57 | 242.29 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 217.3 | 240
2026-09-15 | 16:00:00 | 1.3 | 10.4 | 209.92 | 243.78 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 205.4 | 240.8
2026-09-15 | 17:00:00 | 2.1 | 23.8 | 211.11 | 241.5 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 210.7 | 237.6
2026-09-15 | 18:00:00 | 1.8 | 14.7 | 220.35 | 241.4 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.7 | 238.2
2026-09-15 | 19:00:00 | 2.2 | 14.7 | 219.25 | 237.62 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 220.8 | 233.7
2026-09-15 | 20:00:00 | 1.9 | 2.8 | 228.59 | 241.4 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 228.4 | 240.7
2026-09-15 | 21:00:00 | 1.3 | 4.1 | 231.96 | 240.9 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 231.1 | 240.7
2026-09-15 | 22:00:00 | 1 | 3 | 227.79 | 244.68 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 231.1 | 242
2026-09-15 | 23:00:00 | 1 | 1.8 | 233.16 | 241.5 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 233.9 | 241.7
2026-09-16 | 00:00:00 | 0.9 | 1.8 | 238.32 | 243.48 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 235 | 243.5
2026-09-16 | 01:00:00 | 0.8 | 3.5 | 238.12 | 243.98 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 238.2 | 243.5
2026-09-16 | 02:00:00 | 0.8 | 3.4 | 238.92 | 245.17 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 237.6 | 243.4
2026-09-16 | 03:00:00 | 0.8 | 2.3 | 236.43 | 244.08 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 237 | 242.3
2026-09-16 | 04:00:00 | 0.8 | 3.7 | 231.57 | 242.79 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 231.7 | 239.7
2026-09-16 | 05:00:00 | 0.9 | 12.8 | 225.31 | 244.48 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 228.7 | 243.3
2026-09-16 | 06:00:00 | 0.9 | 13.8 | 221.74 | 243.48 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 224 | 241.4
2026-09-16 | 07:00:00 | 1.1 | 12.9 | 216.08 | 247.46 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 215.1 | 245.9
2026-09-16 | 08:00:00 | 1.1 | 17 | 216.57 | 246.56 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 218.9 | 243.2
2026-09-16 | 09:00:00 | 1.2 | 19 | 214.09 | 241.6 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 217.6 | 239.1
2026-09-16 | 10:00:00 | 1.1 | 26.9 | 213.89 | 240.11 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 219.6 | 237.6
2026-09-16 | 11:00:00 | 1.2 | 22.3 | 221.14 | 239.51 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 225 | 238.4
2026-09-16 | 12:00:00 | 1 | 3.5 | 218.26 | 242.09 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 218.2 | 241.1
2026-09-16 | 13:00:00 | 1 | 2.1 | 222.33 | 237.43 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 220.4 | 237.6
2026-09-16 | 14:00:00 | 1 | 12.8 | 220.05 | 240.5 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 222.7 | 239.6
2026-09-16 | 15:00:00 | 1.3 | 12.4 | 213.59 | 239.11 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 211.2 | 234.4
2026-09-16 | 16:00:00 | 1.1 | 28.9 | 201.88 | 236.73 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 198.8 | 231.4
2026-09-16 | 17:00:00 | 2 | 23.8 | 206.74 | 239.61 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 231.4 | 231.4
2026-09-16 | 18:00:00 | 2.4 | 13.1 | 211.41 | 238.52 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 219 | 238.7
2026-09-16 | 19:00:00 | 1.8 | 13.3 | 222.83 | 243.58 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 226.8 | 242.6
2026-09-16 | 20:00:00 | 1.7 | 14.3 | 224.91 | 243.19 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 229.5 | 242.2
2026-09-16 | 21:00:00 | 1.2 | 4 | 237.23 | 245.37 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 238.7 | 238.7
2026-09-16 | 22:00:00 | 1 | 4.3 | 237.43 | 245.37 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 235.9 | 241.4
2026-09-16 | 23:00:00 | 1 | 3.8 | 235.24 | 243.78 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 233.3 | 240.2
2026-09-17 | 00:00:00 | 0.9 | 2.3 | 236.53 | 243.58 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 233.3 | 242.6
2026-09-17 | 01:00:00 | 0.8 | 3.4 | 234.94 | 243.38 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 229.8 | 242.6
2026-09-17 | 02:00:00 | 0.8 | 3.7 | 235.04 | 243.68 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 235.3 | 241.4
2026-09-17 | 03:00:00 | 0.8 | 3.9 | 235.84 | 242.59 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 234.7 | 241.4
2026-09-17 | 04:00:00 | 1 | 2.4 | 233.45 | 244.48 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 234.4 | 244.7
2026-09-17 | 05:00:00 | 0.9 | 1.9 | 230.48 | 249.84 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 231.5 | 246.9
2026-09-17 | 06:00:00 | 0.9 | 23.6 | 209.82 | 241.89 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 206.9 | 240.8
2026-09-17 | 07:00:00 | 0.9 | 23.6 | 207.74 | 242.59 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 215.8 | 238.7
2026-09-17 | 08:00:00 | 0.9 | 12.1 | 224.42 | 251.63 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.9 | 251.6
2026-09-17 | 09:00:00 | 1.1 | 18.1 | 224.82 | 246.36 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 229.1 | 243.9
2026-09-17 | 10:00:00 | 0.9 | 9.3 | 214.79 | 242.19 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 214.9 | 243.2
2026-09-17 | 11:00:00 | 0.9 | 1.8 | 223.82 | 243.48 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 220.4 | 240.8
2026-09-17 | 12:00:00 | 0.9 | 12.8 | 223.72 | 241.6 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 225 | 239.5
2026-09-17 | 13:00:00 | 0.9 | 3.5 | 235.44 | 246.16 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 238.7 | 244.7
2026-09-17 | 14:00:00 | 1.6 | 18 | 221.34 | 243.29 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 220.4 | 244.6
2026-09-17 | 15:00:00 | 2.3 | 12.8 | 218.06 | 238.62 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 211.6 | 239.9
2026-09-17 | 16:00:00 | 1.9 | 15.2 | 203.27 | 240.8 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 200.7 | 240.8
2026-09-17 | 17:00:00 | 2 | 8.7 | 214.59 | 243.19 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 209.3 | 242.2
2026-09-17 | 18:00:00 | 1.9 | 13.1 | 221.74 | 240.21 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 221.7 | 238.4
2026-09-17 | 19:00:00 | 1.8 | 24.8 | 221.84 | 242.29 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 225 | 239.3
2026-09-17 | 20:00:00 | 1.8 | 4 | 223.72 | 240.11 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 223.3 | 237.9
2026-09-17 | 21:00:00 | 1.2 | 4.9 | 232.76 | 241.89 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 231.5 | 238.7
2026-09-17 | 22:00:00 | 1 | 3.6 | 235.64 | 242.09 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 238.2 | 238.7
2026-09-17 | 23:00:00 | 0.9 | 1.8 | 237.62 | 242.29 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 238.7 | 239
2026-09-18 | 00:00:00 | 1 | 3.6 | 238.02 | 242.89 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 234.7 | 240.8
2026-09-18 | 01:00:00 | 0.8 | 1.8 | 239.41 | 244.18 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 240.3 | 241.4
2026-09-18 | 02:00:00 | 0.8 | 3.5 | 240.11 | 244.48 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 241.4 | 242
2026-09-18 | 03:00:00 | 0.8 | 2.1 | 237.53 | 243.29 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 236.1 | 242
2026-09-18 | 04:00:00 | 0.8 | 12.1 | 232.16 | 243.98 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 233.9 | 242
2026-09-18 | 05:00:00 | 1 | 12.8 | 226.4 | 247.75 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 224.5 | 247.5
2026-09-18 | 06:00:00 | 1 | 17.9 | 218.26 | 244.08 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 213.5 | 240.8
2026-09-18 | 07:00:00 | 1.4 | 12.3 | 225.01 | 244.48 | 2.78 | 2.78 | 231.4 | 231.4 | 0.31 | 0.31 | 233.9 | 233.9 | 0 | 0 | 223.5 | 243.7